## Title
BMS Gateway Controller
GW100K
BMS Register Table
Document: 9590-3038-03 V1.0.1 251803
This Gateway translates Modbus RTU protocol communication from an ActronAir ICUNO-MOD card to one of the following: BACnet/IP, Modbus TCP/IP, or BACnet MS/TP. It is compatible with the ActronAir Advance, Aires, Classic Series 2, and VCC product ranges. The Gateway supports connection of up to 10 ActronAir systems via an ICUNO-MOD per unit (ICUNO-MODs are purchased separately). Information about BMS configuration and unit operation is not included in this document; please refer to the respective ICUNO-MOD and system manuals for detailed instructions. https://docs.actronair.com.au/

## Device 1
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
1 | Set Master Setpoint Temperature | HoldingRegister | 1 | Real | AnalogValue | A101 | 517 | 16 | 30 | DegreesCelsius | R/W
1 | Economiser Temperature Difference | HoldingRegister | 5 | Real | AnalogValue | A103 | 519 | 0 | 10 | DegreesCelsius | R/W
1 | Economiser Outside Min Temperature | HoldingRegister | 7 | Real | AnalogValue | A104 | 520 | 0 | 22.5 | DegreesCelsius | R/W
1 | Economiser Outside Max Temperature | HoldingRegister | 9 | Real | AnalogValue | A105 | 521 | 0 | 26 | DegreesCelsius | R/W
1 | Economiser Minimum Damper | HoldingRegister | 11 | Real | AnalogValue | A106 | 522 | 0 | 10 | Volts | R/W
1 | Economiser Maximum Damper | HoldingRegister | 13 | Real | AnalogValue | A107 | 523 | 0 | 10 | Volts | R/W
1 | Economiser Outside Max Moisture | HoldingRegister | 15 | Real | AnalogValue | A108 | 524 | 0 | 100 | GramsPerKilogram | R/W
1 | Economiser Outside Max Dew Point | HoldingRegister | 17 | Real | AnalogValue | A109 | 525 | 0 | 100 | DegreesCelsius | R/W
1 | Economiser Outside Max Enthalpy | HoldingRegister | 21 | Real | AnalogValue | A110 | 527 | 0 | 100 | KilojoulesPerKilogram | R/W
1 | Economiser Enthalpy Delta | HoldingRegister | 23 | Real | AnalogValue | A111 | 528 | 0 | 10 | KilojoulesPerKilogram | R/W
1 | Economiser CO₂ Minimum Damper | HoldingRegister | 25 | Real | AnalogValue | A112 | 529 | 0 | 10 | Volts | R/W
1 | Economiser CO₂ Maximum Damper | HoldingRegister | 27 | Real | AnalogValue | A113 | 530 | 0 | 10 | Volts | R/W
1 | Room Temperature | InputRegister | 2 | Real | AnalogValue | A115 | 869 | -99.9 | 99.9 | DegreesCelsius | R
1 | Indoor Room Temperature | InputRegister | 4 | Real | AnalogValue | A116 | 870 | -99.9 | 99.9 | DegreesCelsius | R
1 | Outside Temperature | InputRegister | 6 | Real | AnalogValue | A117 | 871 | -99.9 | 99.9 | DegreesCelsius | R
1 | Outside Air Temperature | InputRegister | 8 | Real | AnalogValue | A118 | 872 | -99.9 | 99.9 | DegreesCelsius | R
1 | Compressor 1 Suction Temperature | InputRegister | 10 | Real | AnalogValue | A119 | 873 | -999.9 | 999.9 | DegreesCelsius | R
1 | Compressor 1 Discharge Temperature | InputRegister | 12 | Real | AnalogValue | A120 | 874 | -999.9 | 999.9 | DegreesCelsius | R
1 | Compressor 1 Suction SuperHeat | InputRegister | 14 | Real | AnalogValue | A121 | 875 | -99.9 | 99.9 | DegreesCelsius | R
1 | Compressor 1 Suction SuperHeat Target | InputRegister | 16 | Real | AnalogValue | A122 | 876 | -99.9 | 99.9 | DegreesCelsius | R
1 | Outdoor Coil 1 Temperature | InputRegister | 18 | Real | AnalogValue | A123 | 877 | -99.9 | 99.9 | DegreesCelsius | R
1 | Indoor Coil 1 Temperature | InputRegister | 20 | Real | AnalogValue | A124 | 878 | -99.9 | 99.9 | DegreesCelsius | R
1 | Wall Control 1 Temperature | InputRegister | 22 | Real | AnalogValue | A125 | 879 | -99.9 | 99.9 | DegreesCelsius | R
1 | Wall Control 2 Temperature | InputRegister | 24 | Real | AnalogValue | A126 | 880 | -99.9 | 99.9 | DegreesCelsius | R
1 | Wall Control 3 Temperature | InputRegister | 26 | Real | AnalogValue | A127 | 881 | -99.9 | 99.9 | DegreesCelsius | R
1 | Auxillary Sensor 1 Temperature | InputRegister | 28 | Real | AnalogValue | A128 | 882 | -99.9 | 99.9 | DegreesCelsius | R
1 | Auxillary Sensor 2 Temperature | InputRegister | 30 | Real | AnalogValue | A129 | 883 | -99.9 | 99.9 | DegreesCelsius | R
1 | Auxillary Sensor 3 Temperature | InputRegister | 32 | Real | AnalogValue | A130 | 884 | -99.9 | 99.9 | DegreesCelsius | R
1 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 29 | Real | AnalogValue | A131 | 531 | 0 | 100 | Percent | R/W
1 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 31 | Real | AnalogValue | A132 | 532 | 0 | 100 | Percent | R/W
1 | Reduced Airflow Speed | HoldingRegister | 33 | Real | AnalogValue | A133 | 533 | 0 | 100 | Percent | R/W
1 | Economiser Outside Max Humidity | HoldingRegister | 35 | Real | AnalogValue | A134 | 534 | 0 | 100 | Percent | R/W
1 | Actual System Running Capacity | InputRegister | 34 | Real | AnalogValue | A135 | 885 | 0 | 100 | Percent | R
1 | Compressor 1 Demand | InputRegister | 36 | Real | AnalogValue | A136 | 886 | 0 | 100 | Percent | R
1 | Compressor 1 Speed | InputRegister | 38 | Real | AnalogValue | A137 | 887 | 0 | 100 | Percent | R
1 | Indoor Coil 1 Fan Speed | InputRegister | 40 | Real | AnalogValue | A138 | 888 | 0 | 100 | Percent | R
1 | Compressor 1 EEV position | InputRegister | 42 | Real | AnalogValue | A139 | 889 | 0 | 100 | Percent | R
1 | Generic Analog 01 | HoldingRegister | 37 | Real | AnalogValue | A140 | 535 |  |  |  | R/W
1 | Generic Analog 02 | HoldingRegister | 39 | Real | AnalogValue | A141 | 536 |  |  |  | R/W
1 | Generic Analog 03 | HoldingRegister | 41 | Real | AnalogValue | A142 | 537 |  |  |  | R/W
1 | Generic Analog 04 | HoldingRegister | 43 | Real | AnalogValue | A143 | 538 |  |  |  | R/W
1 | Generic Analog 05 | HoldingRegister | 45 | Real | AnalogValue | A144 | 539 |  |  |  | R/W
1 | Turns the AC Off/On (0=Off, 1=On) | Coil | 0 | Bool | BinaryValue | D101 | 1 |  |  |  | R/W
1 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 1 | Bool | BinaryValue | D102 | 2 |  |  |  | R/W
1 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 2 | Bool | BinaryValue | D103 | 3 |  |  |  | R/W
1 | Set Turbo Mode (0=Off, 1=On) | Coil | 3 | Bool | BinaryValue | D104 | 4 |  |  |  | R/W
1 | Set Quiet Mode (0=Off, 1=On) | Coil | 4 | Bool | BinaryValue | D105 | 5 |  |  |  | R/W
1 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 5 | Bool | BinaryValue | D106 | 6 |  |  |  | R/W
1 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 8 | Bool | BinaryValue | D109 | 9 |  |  |  | R/W
1 | Enable Economiser (0=Off, 1=On) | Coil | 9 | Bool | BinaryValue | D110 | 10 |  |  |  | R/W
1 | Enable Humidity Control | Coil | 10 | Bool | BinaryValue | D111 | 11 |  |  |  | R/W
1 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 11 | Bool | BinaryValue | D112 | 12 |  |  |  | R/W
1 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 12 | Bool | BinaryValue | D113 | 13 |  |  |  | R/W
1 | Enable CO₂ Control (0=Off, 1=On) | Coil | 13 | Bool | BinaryValue | D114 | 14 |  |  |  | R/W
1 | Alarm Output (0=Off, 1=On) | DiscreteInput | 0 | Bool | BinaryValue | D115 | 276 |  |  |  | R
1 | Air Filter Notification | DiscreteInput | 1 | Bool | BinaryValue | D116 | 277 |  |  |  | R
1 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 4 | Bool | BinaryValue | D119 | 280 |  |  |  | R
1 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 5 | Bool | BinaryValue | D120 | 281 |  |  |  | R
1 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 6 | Bool | BinaryValue | D121 | 282 |  |  |  | R
1 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 7 | Bool | BinaryValue | D122 | 283 |  |  |  | R
1 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 8 | Bool | BinaryValue | D123 | 284 |  |  |  | R
1 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 9 | Bool | BinaryValue | D124 | 285 |  |  |  | R
1 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 10 | Bool | BinaryValue | D125 | 286 |  |  |  | R
1 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 11 | Bool | BinaryValue | D126 | 287 |  |  |  | R
1 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 12 | Bool | BinaryValue | D127 | 288 |  |  |  | R
1 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 13 | Bool | BinaryValue | D128 | 289 |  |  |  | R
1 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 14 | Bool | BinaryValue | D129 | 290 |  |  |  | R
1 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 15 | Bool | BinaryValue | D130 | 291 |  |  |  | R
1 | Compressor 1 Discharge Temp High | DiscreteInput | 16 | Bool | BinaryValue | D131 | 292 |  |  |  | R
1 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 17 | Bool | BinaryValue | D132 | 293 |  |  |  | R
1 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 18 | Bool | BinaryValue | D133 | 294 |  |  |  | R
1 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 19 | Bool | BinaryValue | D134 | 295 |  |  |  | R
1 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 20 | Bool | BinaryValue | D135 | 296 |  |  |  | R
1 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 21 | Bool | BinaryValue | D136 | 297 |  |  |  | R
1 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 22 | Bool | BinaryValue | D137 | 298 |  |  |  | R
1 | Set zone 1 (0=Off, 1=On) | Coil | 14 | Bool | BinaryValue | D138 | 15 |  |  |  | R/W
1 | Set zone 2 (0=Off, 1=On) | Coil | 15 | Bool | BinaryValue | D139 | 16 |  |  |  | R/W
1 | Set zone 3 (0=Off, 1=On) | Coil | 16 | Bool | BinaryValue | D140 | 17 |  |  |  | R/W
1 | Set zone 4 (0=Off, 1=On) | Coil | 17 | Bool | BinaryValue | D141 | 18 |  |  |  | R/W
1 | Set zone 5 (0=Off, 1=On) | Coil | 18 | Bool | BinaryValue | D142 | 19 |  |  |  | R/W
1 | Set zone 6 (0=Off, 1=On) | Coil | 19 | Bool | BinaryValue | D143 | 20 |  |  |  | R/W
1 | Set zone 7 (0=Off, 1=On) | Coil | 20 | Bool | BinaryValue | D144 | 21 |  |  |  | R/W
1 | Set zone 8 (0=Off, 1=On) | Coil | 21 | Bool | BinaryValue | D145 | 22 |  |  |  | R/W
1 | Generic Digital 1 | Coil | 22 | Bool | BinaryValue | D146 | 23 |  |  |  | R/W
1 | Generic Digital 2 | Coil | 23 | Bool | BinaryValue | D147 | 24 |  |  |  | R/W
1 | Generic Digital 3 | Coil | 24 | Bool | BinaryValue | D148 | 25 |  |  |  | R/W
1 | Generic Digital 4 | Coil | 25 | Bool | BinaryValue | D149 | 26 |  |  |  | R/W
1 | Generic Digital 5 | Coil | 26 | Bool | BinaryValue | D150 | 27 |  |  |  | R/W
1 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 47 | Int | IntegerValue | I101 | 540 | 1 | 4 |  | R/W
1 | Set Air Filter Notification Timer | HoldingRegister | 48 | Int | IntegerValue | I102 | 541 | 1 | 10000 | Hours | R/W
1 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 49 | Int | IntegerValue | I103 | 542 | 1 | 4 |  | R/W
1 | Target Airflow | HoldingRegister | 50 | Int | IntegerValue | I104 | 543 | 0 | 6000 | LitersPerSecond | R/W
1 | Enable Volumetric Airflow | HoldingRegister | 51 | Int | IntegerValue | I105 | 544 | 0 | 6000 | LitersPerSecond | R/W
1 | Indoor Pressure Filter level warning | HoldingRegister | 52 | Int | IntegerValue | I106 | 545 | 0 | 6000 | Pascals | R/W
1 | Economiser CO₂ Low Level | HoldingRegister | 53 | Int | IntegerValue | I107 | 546 | 0 | 1000 | PartsPerMillion | R/W
1 | Economiser CO₂ High Level | HoldingRegister | 54 | Int | IntegerValue | I108 | 547 | 0 | 1000 | PartsPerMillion | R/W
1 | BMS card Software version | InputRegister | 44 | Int | IntegerValue | I109 | 890 | 0 | 32767 |  | R
1 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 45 | Int | IntegerValue | I110 | 891 | 0 | 2 |  | R
1 | Air Filter Run Timer | InputRegister | 46 | Int | IntegerValue | I111 | 892 | 0 | 10000 | Hours | R
1 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 47 | Int | IntegerValue | I112 | 893 | 0 | 4 |  | R
1 | Indoor Airflow | InputRegister | 48 | Int | IntegerValue | I113 | 894 | 0 | 6000 | LitersPerSecond | R
1 | Indoor Static Pressure | InputRegister | 49 | Int | IntegerValue | I114 | 895 | 0 | 6000 | Pascals | R
1 | Measured CO₂ level | InputRegister | 50 | Int | IntegerValue | I115 | 896 | 0 | 1000 | PartsPerMillion | R
1 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 51 | Int | IntegerValue | I116 | 897 | 0 | 100 |  | R
1 | Error History Log, 1 error ago | InputRegister | 52 | Int | IntegerValue | I117 | 898 | 0 | 100 |  | R
1 | Error History Log, 2 errors ago | InputRegister | 53 | Int | IntegerValue | I118 | 899 | 0 | 100 |  | R
1 | Error History Log, 3 errors ago | InputRegister | 54 | Int | IntegerValue | I119 | 900 | 0 | 100 |  | R
1 | Error History Log, 4 errors ago | InputRegister | 55 | Int | IntegerValue | I120 | 901 | 0 | 100 |  | R
1 | Error History Log, 5 errors ago | InputRegister | 56 | Int | IntegerValue | I121 | 902 | 0 | 100 |  | R
1 | Outdoor Unit 1 Model | InputRegister | 57 | Int | IntegerValue | I122 | 903 | 0 | 32767 |  | R
1 | Outdoor Unit 1 Software version | InputRegister | 58 | Int | IntegerValue | I123 | 904 | 0 | 32767 |  | R
1 | Compressor 1 Type | InputRegister | 59 | Int | IntegerValue | I124 | 905 | 0 | 100 |  | R
1 | Compressor 1 Suction Pressure | InputRegister | 60 | Int | IntegerValue | I125 | 906 | 0 | 6000 | KiloPascals | R
1 | Compressor 1 Discharge Pressure | InputRegister | 61 | Int | IntegerValue | I126 | 907 | 0 | 6000 | KiloPascals | R
1 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 62 | Int | IntegerValue | I127 | 908 | 0 | 3 |  | R
1 | Indoor Coil 1 Fan 1 Speed | InputRegister | 63 | Int | IntegerValue | I128 | 909 | 0 | 9999 | RevolutionsPerMinute | R
1 | Generic Integer 1 | HoldingRegister | 55 | Int | IntegerValue | I129 | 548 |  |  |  | R/W
1 | Generic Integer 2 | HoldingRegister | 56 | Int | IntegerValue | I130 | 549 |  |  |  | R/W
1 | Generic Integer 3 | HoldingRegister | 57 | Int | IntegerValue | I131 | 550 |  |  |  | R/W
1 | Generic Integer 4 | HoldingRegister | 58 | Int | IntegerValue | I132 | 551 |  |  |  | R/W
1 | Generic Integer 5 | HoldingRegister | 59 | Int | IntegerValue | I133 | 552 |  |  |  | R/W

## Device 2
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
2 | Set Master Setpoint Temperature | HoldingRegister | 70 | Real | AnalogValue | A201 | 553 | 16 | 30 | DegreesCelsius | R/W
2 | Economiser Temperature Difference | HoldingRegister | 74 | Real | AnalogValue | A203 | 555 | 0 | 10 | DegreesCelsius | R/W
2 | Economiser Outside Min Temperature | HoldingRegister | 76 | Real | AnalogValue | A204 | 556 | 0 | 22.5 | DegreesCelsius | R/W
2 | Economiser Outside Max Temperature | HoldingRegister | 78 | Real | AnalogValue | A205 | 557 | 0 | 26 | DegreesCelsius | R/W
2 | Economiser Minimum Damper | HoldingRegister | 80 | Real | AnalogValue | A206 | 558 | 0 | 10 | Volts | R/W
2 | Economiser Maximum Damper | HoldingRegister | 82 | Real | AnalogValue | A207 | 559 | 0 | 10 | Volts | R/W
2 | Economiser Outside Max Moisture | HoldingRegister | 84 | Real | AnalogValue | A208 | 560 | 0 | 100 | GramsPerKilogram | R/W
2 | Economiser Outside Max Dew Point | HoldingRegister | 86 | Real | AnalogValue | A209 | 561 | 0 | 100 | DegreesCelsius | R/W
2 | Economiser Outside Max Enthalpy | HoldingRegister | 88 | Real | AnalogValue | A210 | 562 | 0 | 100 | KilojoulesPerKilogram | R/W
2 | Economiser Enthalpy Delta | HoldingRegister | 90 | Real | AnalogValue | A211 | 563 | 0 | 10 | KilojoulesPerKilogram | R/W
2 | Economiser CO₂ Minimum Damper | HoldingRegister | 92 | Real | AnalogValue | A212 | 564 | 0 | 10 | Volts | R/W
2 | Economiser CO₂ Maximum Damper | HoldingRegister | 94 | Real | AnalogValue | A213 | 565 | 0 | 10 | Volts | R/W
2 | Room Temperature | InputRegister | 72 | Real | AnalogValue | A215 | 911 | -99.9 | 99.9 | DegreesCelsius | R
2 | Indoor Room Temperature | InputRegister | 74 | Real | AnalogValue | A216 | 912 | -99.9 | 99.9 | DegreesCelsius | R
2 | Outside Temperature | InputRegister | 76 | Real | AnalogValue | A217 | 913 | -99.9 | 99.9 | DegreesCelsius | R
2 | Outside Air Temperature | InputRegister | 78 | Real | AnalogValue | A218 | 914 | -99.9 | 99.9 | DegreesCelsius | R
2 | Compressor 1 Suction Temperature | InputRegister | 80 | Real | AnalogValue | A219 | 915 | -999.9 | 999.9 | DegreesCelsius | R
2 | Compressor 1 Discharge Temperature | InputRegister | 82 | Real | AnalogValue | A220 | 916 | -999.9 | 999.9 | DegreesCelsius | R
2 | Compressor 1 Suction SuperHeat | InputRegister | 84 | Real | AnalogValue | A221 | 917 | -99.9 | 99.9 | DegreesCelsius | R
2 | Compressor 1 Suction SuperHeat Target | InputRegister | 86 | Real | AnalogValue | A222 | 918 | -99.9 | 99.9 | DegreesCelsius | R
2 | Outdoor Coil 1 Temperature | InputRegister | 88 | Real | AnalogValue | A223 | 919 | -99.9 | 99.9 | DegreesCelsius | R
2 | Indoor Coil 1 Temperature | InputRegister | 90 | Real | AnalogValue | A224 | 920 | -99.9 | 99.9 | DegreesCelsius | R
2 | Wall Control 1 Temperature | InputRegister | 92 | Real | AnalogValue | A225 | 921 | -99.9 | 99.9 | DegreesCelsius | R
2 | Wall Control 2 Temperature | InputRegister | 94 | Real | AnalogValue | A226 | 922 | -99.9 | 99.9 | DegreesCelsius | R
2 | Wall Control 3 Temperature | InputRegister | 96 | Real | AnalogValue | A227 | 923 | -99.9 | 99.9 | DegreesCelsius | R
2 | Auxillary Sensor 1 Temperature | InputRegister | 98 | Real | AnalogValue | A228 | 924 | -99.9 | 99.9 | DegreesCelsius | R
2 | Auxillary Sensor 2 Temperature | InputRegister | 100 | Real | AnalogValue | A229 | 925 | -99.9 | 99.9 | DegreesCelsius | R
2 | Auxillary Sensor 3 Temperature | InputRegister | 102 | Real | AnalogValue | A230 | 926 | -99.9 | 99.9 | DegreesCelsius | R
2 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 96 | Real | AnalogValue | A231 | 566 | 0 | 100 | Percent | R/W
2 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 98 | Real | AnalogValue | A232 | 567 | 0 | 100 | Percent | R/W
2 | Reduced Airflow Speed | HoldingRegister | 100 | Real | AnalogValue | A233 | 568 | 0 | 100 | Percent | R/W
2 | Economiser Outside Max Humidity | HoldingRegister | 102 | Real | AnalogValue | A234 | 569 | 0 | 100 | Percent | R/W
2 | Actual System Running Capacity | InputRegister | 104 | Real | AnalogValue | A235 | 927 | 0 | 100 | Percent | R
2 | Compressor 1 Demand | InputRegister | 106 | Real | AnalogValue | A236 | 928 | 0 | 100 | Percent | R
2 | Compressor 1 Speed | InputRegister | 108 | Real | AnalogValue | A237 | 929 | 0 | 100 | Percent | R
2 | Indoor Coil 1 Fan Speed | InputRegister | 110 | Real | AnalogValue | A238 | 930 | 0 | 100 | Percent | R
2 | Compressor 1 EEV position | InputRegister | 112 | Real | AnalogValue | A239 | 931 | 0 | 100 | Percent | R
2 | Generic Analog 01 | HoldingRegister | 104 | Real | AnalogValue | A240 | 570 |  |  |  | R/W
2 | Generic Analog 02 | HoldingRegister | 106 | Real | AnalogValue | A241 | 571 |  |  |  | R/W
2 | Generic Analog 03 | HoldingRegister | 108 | Real | AnalogValue | A242 | 572 |  |  |  | R/W
2 | Generic Analog 04 | HoldingRegister | 110 | Real | AnalogValue | A243 | 573 |  |  |  | R/W
2 | Generic Analog 05 | HoldingRegister | 112 | Real | AnalogValue | A244 | 574 |  |  |  | R/W
2 | Turns the AC Off/On (0=Off, 1=On) | Coil | 30 | Bool | BinaryValue | D201 | 28 |  |  |  | R/W
2 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 31 | Bool | BinaryValue | D202 | 29 |  |  |  | R/W
2 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 32 | Bool | BinaryValue | D203 | 30 |  |  |  | R/W
2 | Set Turbo Mode (0=Off, 1=On) | Coil | 34 | Bool | BinaryValue | D204 | 31 |  |  |  | R/W
2 | Set Quiet Mode (0=Off, 1=On) | Coil | 35 | Bool | BinaryValue | D205 | 32 |  |  |  | R/W
2 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 36 | Bool | BinaryValue | D206 | 33 |  |  |  | R/W
2 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 39 | Bool | BinaryValue | D209 | 36 |  |  |  | R/W
2 | Enable Economiser (0=Off, 1=On) | Coil | 40 | Bool | BinaryValue | D210 | 37 |  |  |  | R/W
2 | Enable Humidity Control | Coil | 41 | Bool | BinaryValue | D211 | 38 |  |  |  | R/W
2 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 42 | Bool | BinaryValue | D212 | 39 |  |  |  | R/W
2 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 43 | Bool | BinaryValue | D213 | 40 |  |  |  | R/W
2 | Enable CO₂ Control (0=Off, 1=On) | Coil | 44 | Bool | BinaryValue | D214 | 41 |  |  |  | R/W
2 | Alarm Output (0=Off, 1=On) | DiscreteInput | 30 | Bool | BinaryValue | D215 | 299 |  |  |  | R
2 | Air Filter Notification | DiscreteInput | 31 | Bool | BinaryValue | D216 | 300 |  |  |  | R
2 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 34 | Bool | BinaryValue | D219 | 303 |  |  |  | R
2 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 35 | Bool | BinaryValue | D220 | 304 |  |  |  | R
2 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 36 | Bool | BinaryValue | D221 | 305 |  |  |  | R
2 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 37 | Bool | BinaryValue | D222 | 306 |  |  |  | R
2 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 38 | Bool | BinaryValue | D223 | 307 |  |  |  | R
2 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 39 | Bool | BinaryValue | D224 | 308 |  |  |  | R
2 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 40 | Bool | BinaryValue | D225 | 309 |  |  |  | R
2 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 41 | Bool | BinaryValue | D226 | 310 |  |  |  | R
2 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 42 | Bool | BinaryValue | D227 | 311 |  |  |  | R
2 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 43 | Bool | BinaryValue | D228 | 312 |  |  |  | R
2 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 44 | Bool | BinaryValue | D229 | 313 |  |  |  | R
2 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 45 | Bool | BinaryValue | D230 | 314 |  |  |  | R
2 | Compressor 1 Discharge Temp High | DiscreteInput | 46 | Bool | BinaryValue | D231 | 315 |  |  |  | R
2 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 47 | Bool | BinaryValue | D232 | 316 |  |  |  | R
2 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 48 | Bool | BinaryValue | D233 | 317 |  |  |  | R
2 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 49 | Bool | BinaryValue | D234 | 318 |  |  |  | R
2 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 50 | Bool | BinaryValue | D235 | 319 |  |  |  | R
2 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 51 | Bool | BinaryValue | D236 | 320 |  |  |  | R
2 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 52 | Bool | BinaryValue | D237 | 321 |  |  |  | R
2 | Set zone 1 (0=Off, 1=On) | Coil | 45 | Bool | BinaryValue | D238 | 42 |  |  |  | R/W
2 | Set zone 2 (0=Off, 1=On) | Coil | 46 | Bool | BinaryValue | D239 | 43 |  |  |  | R/W
2 | Set zone 3 (0=Off, 1=On) | Coil | 47 | Bool | BinaryValue | D240 | 44 |  |  |  | R/W
2 | Set zone 4 (0=Off, 1=On) | Coil | 48 | Bool | BinaryValue | D241 | 45 |  |  |  | R/W
2 | Set zone 5 (0=Off, 1=On) | Coil | 49 | Bool | BinaryValue | D242 | 46 |  |  |  | R/W
2 | Set zone 6 (0=Off, 1=On) | Coil | 50 | Bool | BinaryValue | D243 | 47 |  |  |  | R/W
2 | Set zone 7 (0=Off, 1=On) | Coil | 51 | Bool | BinaryValue | D244 | 48 |  |  |  | R/W
2 | Set zone 8 (0=Off, 1=On) | Coil | 52 | Bool | BinaryValue | D245 | 49 |  |  |  | R/W
2 | Generic Digital 1 | Coil | 53 | Bool | BinaryValue | D246 | 50 |  |  |  | R/W
2 | Generic Digital 2 | Coil | 54 | Bool | BinaryValue | D247 | 51 |  |  |  | R/W
2 | Generic Digital 3 | Coil | 55 | Bool | BinaryValue | D248 | 52 |  |  |  | R/W
2 | Generic Digital 4 | Coil | 56 | Bool | BinaryValue | D249 | 53 |  |  |  | R/W
2 | Generic Digital 5 | Coil | 57 | Bool | BinaryValue | D250 | 54 |  |  |  | R/W
2 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 114 | Int | IntegerValue | I201 | 575 | 1 | 4 |  | R/W
2 | Set Air Filter Notification Timer | HoldingRegister | 115 | Int | IntegerValue | I202 | 576 | 1 | 10000 | Hours | R/W
2 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 116 | Int | IntegerValue | I203 | 577 | 1 | 4 |  | R/W
2 | Target Airflow | HoldingRegister | 117 | Int | IntegerValue | I204 | 578 | 0 | 6000 | LitersPerSecond | R/W
2 | Enable Volumetric Airflow | HoldingRegister | 118 | Int | IntegerValue | I205 | 579 | 0 | 6000 | LitersPerSecond | R/W
2 | Indoor Pressure Filter level warning | HoldingRegister | 119 | Int | IntegerValue | I206 | 580 | 0 | 6000 | Pascals | R/W
2 | Economiser CO₂ Low Level | HoldingRegister | 120 | Int | IntegerValue | I207 | 581 | 0 | 1000 | PartsPerMillion | R/W
2 | Economiser CO₂ High Level | HoldingRegister | 121 | Int | IntegerValue | I208 | 582 | 0 | 1000 | PartsPerMillion | R/W
2 | BMS card Software version | InputRegister | 114 | Int | IntegerValue | I209 | 932 | 0 | 32767 |  | R
2 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 115 | Int | IntegerValue | I210 | 933 | 0 | 2 |  | R
2 | Air Filter Run Timer | InputRegister | 116 | Int | IntegerValue | I211 | 934 | 0 | 10000 | Hours | R
2 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 117 | Int | IntegerValue | I212 | 935 | 0 | 4 |  | R
2 | Indoor Airflow | InputRegister | 118 | Int | IntegerValue | I213 | 936 | 0 | 6000 | LitersPerSecond | R
2 | Indoor Static Pressure | InputRegister | 119 | Int | IntegerValue | I214 | 937 | 0 | 6000 | Pascals | R
2 | Measured CO₂ level | InputRegister | 120 | Int | IntegerValue | I215 | 938 | 0 | 1000 | PartsPerMillion | R
2 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 121 | Int | IntegerValue | I216 | 939 | 0 | 100 |  | R
2 | Error History Log, 1 error ago | InputRegister | 122 | Int | IntegerValue | I217 | 940 | 0 | 100 |  | R
2 | Error History Log, 2 errors ago | InputRegister | 123 | Int | IntegerValue | I218 | 941 | 0 | 100 |  | R
2 | Error History Log, 3 errors ago | InputRegister | 124 | Int | IntegerValue | I219 | 942 | 0 | 100 |  | R
2 | Error History Log, 4 errors ago | InputRegister | 125 | Int | IntegerValue | I220 | 943 | 0 | 100 |  | R
2 | Error History Log, 5 errors ago | InputRegister | 126 | Int | IntegerValue | I221 | 944 | 0 | 100 |  | R
2 | Outdoor Unit 1 Model | InputRegister | 127 | Int | IntegerValue | I222 | 945 | 0 | 32767 |  | R
2 | Outdoor Unit 1 Software version | InputRegister | 128 | Int | IntegerValue | I223 | 946 | 0 | 32767 |  | R
2 | Compressor 1 Type | InputRegister | 129 | Int | IntegerValue | I224 | 947 | 0 | 100 |  | R
2 | Compressor 1 Suction Pressure | InputRegister | 130 | Int | IntegerValue | I225 | 948 | 0 | 6000 | KiloPascals | R
2 | Compressor 1 Discharge Pressure | InputRegister | 131 | Int | IntegerValue | I226 | 949 | 0 | 6000 | KiloPascals | R
2 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 132 | Int | IntegerValue | I227 | 950 | 0 | 3 |  | R
2 | Indoor Coil 1 Fan 1 Speed | InputRegister | 133 | Int | IntegerValue | I228 | 951 | 0 | 9999 | RevolutionsPerMinute | R
2 | Generic Integer 1 | HoldingRegister | 122 | Int | IntegerValue | I229 | 583 |  |  |  | R/W
2 | Generic Integer 2 | HoldingRegister | 123 | Int | IntegerValue | I230 | 584 |  |  |  | R/W
2 | Generic Integer 3 | HoldingRegister | 124 | Int | IntegerValue | I231 | 585 |  |  |  | R/W
2 | Generic Integer 4 | HoldingRegister | 125 | Int | IntegerValue | I232 | 586 |  |  |  | R/W
2 | Generic Integer 5 | HoldingRegister | 126 | Int | IntegerValue | I233 | 587 |  |  |  | R/W

## Device 3
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
3 | Set Master Setpoint Temperature | HoldingRegister | 140 | Real | AnalogValue | A301 | 588 | 16 | 30 | DegreesCelsius | R/W
3 | Economiser Temperature Difference | HoldingRegister | 144 | Real | AnalogValue | A303 | 590 | 0 | 10 | DegreesCelsius | R/W
3 | Economiser Outside Min Temperature | HoldingRegister | 146 | Real | AnalogValue | A304 | 591 | 0 | 22.5 | DegreesCelsius | R/W
3 | Economiser Outside Max Temperature | HoldingRegister | 148 | Real | AnalogValue | A305 | 592 | 0 | 26 | DegreesCelsius | R/W
3 | Economiser Minimum Damper | HoldingRegister | 150 | Real | AnalogValue | A306 | 593 | 0 | 10 | Volts | R/W
3 | Economiser Maximum Damper | HoldingRegister | 152 | Real | AnalogValue | A307 | 594 | 0 | 10 | Volts | R/W
3 | Economiser Outside Max Moisture | HoldingRegister | 154 | Real | AnalogValue | A308 | 595 | 0 | 100 | GramsPerKilogram | R/W
3 | Economiser Outside Max Dew Point | HoldingRegister | 156 | Real | AnalogValue | A309 | 596 | 0 | 100 | DegreesCelsius | R/W
3 | Economiser Outside Max Enthalpy | HoldingRegister | 158 | Real | AnalogValue | A310 | 597 | 0 | 100 | KilojoulesPerKilogram | R/W
3 | Economiser Enthalpy Delta | HoldingRegister | 160 | Real | AnalogValue | A311 | 598 | 0 | 10 | KilojoulesPerKilogram | R/W
3 | Economiser CO₂ Minimum Damper | HoldingRegister | 162 | Real | AnalogValue | A312 | 599 | 0 | 10 | Volts | R/W
3 | Economiser CO₂ Maximum Damper | HoldingRegister | 164 | Real | AnalogValue | A313 | 600 | 0 | 10 | Volts | R/W
3 | Room Temperature | InputRegister | 142 | Real | AnalogValue | A315 | 953 | -99.9 | 99.9 | DegreesCelsius | R
3 | Indoor Room Temperature | InputRegister | 144 | Real | AnalogValue | A316 | 954 | -99.9 | 99.9 | DegreesCelsius | R
3 | Outside Temperature | InputRegister | 146 | Real | AnalogValue | A317 | 955 | -99.9 | 99.9 | DegreesCelsius | R
3 | Outside Air Temperature | InputRegister | 148 | Real | AnalogValue | A318 | 956 | -99.9 | 99.9 | DegreesCelsius | R
3 | Compressor 1 Suction Temperature | InputRegister | 150 | Real | AnalogValue | A319 | 957 | -999.9 | 999.9 | DegreesCelsius | R
3 | Compressor 1 Discharge Temperature | InputRegister | 152 | Real | AnalogValue | A320 | 958 | -999.9 | 999.9 | DegreesCelsius | R
3 | Compressor 1 Suction SuperHeat | InputRegister | 154 | Real | AnalogValue | A321 | 959 | -99.9 | 99.9 | DegreesCelsius | R
3 | Compressor 1 Suction SuperHeat Target | InputRegister | 156 | Real | AnalogValue | A322 | 960 | -99.9 | 99.9 | DegreesCelsius | R
3 | Outdoor Coil 1 Temperature | InputRegister | 158 | Real | AnalogValue | A323 | 961 | -99.9 | 99.9 | DegreesCelsius | R
3 | Indoor Coil 1 Temperature | InputRegister | 160 | Real | AnalogValue | A324 | 962 | -99.9 | 99.9 | DegreesCelsius | R
3 | Wall Control 1 Temperature | InputRegister | 162 | Real | AnalogValue | A325 | 963 | -99.9 | 99.9 | DegreesCelsius | R
3 | Wall Control 2 Temperature | InputRegister | 164 | Real | AnalogValue | A326 | 964 | -99.9 | 99.9 | DegreesCelsius | R
3 | Wall Control 3 Temperature | InputRegister | 166 | Real | AnalogValue | A327 | 965 | -99.9 | 99.9 | DegreesCelsius | R
3 | Auxillary Sensor 1 Temperature | InputRegister | 168 | Real | AnalogValue | A328 | 966 | -99.9 | 99.9 | DegreesCelsius | R
3 | Auxillary Sensor 2 Temperature | InputRegister | 170 | Real | AnalogValue | A329 | 967 | -99.9 | 99.9 | DegreesCelsius | R
3 | Auxillary Sensor 3 Temperature | InputRegister | 172 | Real | AnalogValue | A330 | 968 | -99.9 | 99.9 | DegreesCelsius | R
3 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 166 | Real | AnalogValue | A331 | 601 | 0 | 100 | Percent | R/W
3 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 168 | Real | AnalogValue | A332 | 602 | 0 | 100 | Percent | R/W
3 | Reduced Airflow Speed | HoldingRegister | 170 | Real | AnalogValue | A333 | 603 | 0 | 100 | Percent | R/W
3 | Economiser Outside Max Humidity | HoldingRegister | 172 | Real | AnalogValue | A334 | 604 | 0 | 100 | Percent | R/W
3 | Actual System Running Capacity | InputRegister | 174 | Real | AnalogValue | A335 | 969 | 0 | 100 | Percent | R
3 | Compressor 1 Demand | InputRegister | 176 | Real | AnalogValue | A336 | 970 | 0 | 100 | Percent | R
3 | Compressor 1 Speed | InputRegister | 178 | Real | AnalogValue | A337 | 971 | 0 | 100 | Percent | R
3 | Indoor Coil 1 Fan Speed | InputRegister | 180 | Real | AnalogValue | A338 | 972 | 0 | 100 | Percent | R
3 | Compressor 1 EEV position | InputRegister | 182 | Real | AnalogValue | A339 | 973 | 0 | 100 | Percent | R
3 | Generic Analog 01 | HoldingRegister | 174 | Real | AnalogValue | A340 | 605 |  |  |  | R/W
3 | Generic Analog 02 | HoldingRegister | 176 | Real | AnalogValue | A341 | 606 |  |  |  | R/W
3 | Generic Analog 03 | HoldingRegister | 178 | Real | AnalogValue | A342 | 607 |  |  |  | R/W
3 | Generic Analog 04 | HoldingRegister | 180 | Real | AnalogValue | A343 | 608 |  |  |  | R/W
3 | Generic Analog 05 | HoldingRegister | 182 | Real | AnalogValue | A344 | 609 |  |  |  | R/W
3 | Turns the AC Off/On (0=Off, 1=On) | Coil | 60 | Bool | BinaryValue | D301 | 55 |  |  |  | R/W
3 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 61 | Bool | BinaryValue | D302 | 56 |  |  |  | R/W
3 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 62 | Bool | BinaryValue | D303 | 57 |  |  |  | R/W
3 | Set Turbo Mode (0=Off, 1=On) | Coil | 63 | Bool | BinaryValue | D304 | 58 |  |  |  | R/W
3 | Set Quiet Mode (0=Off, 1=On) | Coil | 64 | Bool | BinaryValue | D305 | 59 |  |  |  | R/W
3 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 65 | Bool | BinaryValue | D306 | 60 |  |  |  | R/W
3 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 68 | Bool | BinaryValue | D309 | 63 |  |  |  | R/W
3 | Enable Economiser (0=Off, 1=On) | Coil | 69 | Bool | BinaryValue | D310 | 64 |  |  |  | R/W
3 | Enable Humidity Control | Coil | 70 | Bool | BinaryValue | D311 | 65 |  |  |  | R/W
3 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 71 | Bool | BinaryValue | D312 | 66 |  |  |  | R/W
3 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 72 | Bool | BinaryValue | D313 | 67 |  |  |  | R/W
3 | Enable CO₂ Control (0=Off, 1=On) | Coil | 73 | Bool | BinaryValue | D314 | 68 |  |  |  | R/W
3 | Alarm Output (0=Off, 1=On) | DiscreteInput | 60 | Bool | BinaryValue | D315 | 322 |  |  |  | R
3 | Air Filter Notification | DiscreteInput | 61 | Bool | BinaryValue | D316 | 323 |  |  |  | R
3 | DeSuperHeater Active (0=Off, 1=On) | DiscreteInput | 62 | Bool | BinaryValue | D317 | 324 |  |  |  | R
3 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 65 | Bool | BinaryValue | D320 | 327 |  |  |  | R
3 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 66 | Bool | BinaryValue | D321 | 328 |  |  |  | R
3 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 67 | Bool | BinaryValue | D322 | 329 |  |  |  | R
3 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 68 | Bool | BinaryValue | D323 | 330 |  |  |  | R
3 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 69 | Bool | BinaryValue | D324 | 331 |  |  |  | R
3 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 70 | Bool | BinaryValue | D325 | 332 |  |  |  | R
3 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 71 | Bool | BinaryValue | D326 | 333 |  |  |  | R
3 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 72 | Bool | BinaryValue | D327 | 334 |  |  |  | R
3 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 73 | Bool | BinaryValue | D328 | 335 |  |  |  | R
3 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 74 | Bool | BinaryValue | D329 | 336 |  |  |  | R
3 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 75 | Bool | BinaryValue | D330 | 337 |  |  |  | R
3 | Compressor 1 Discharge Temp High | DiscreteInput | 76 | Bool | BinaryValue | D331 | 338 |  |  |  | R
3 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 77 | Bool | BinaryValue | D332 | 339 |  |  |  | R
3 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 78 | Bool | BinaryValue | D333 | 340 |  |  |  | R
3 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 79 | Bool | BinaryValue | D334 | 341 |  |  |  | R
3 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 80 | Bool | BinaryValue | D335 | 342 |  |  |  | R
3 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 81 | Bool | BinaryValue | D336 | 343 |  |  |  | R
3 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 82 | Bool | BinaryValue | D337 | 344 |  |  |  | R
3 | Set zone 1 (0=Off, 1=On) | Coil | 74 | Bool | BinaryValue | D338 | 69 |  |  |  | R/W
3 | Set zone 2 (0=Off, 1=On) | Coil | 75 | Bool | BinaryValue | D339 | 70 |  |  |  | R/W
3 | Set zone 3 (0=Off, 1=On) | Coil | 76 | Bool | BinaryValue | D340 | 71 |  |  |  | R/W
3 | Set zone 4 (0=Off, 1=On) | Coil | 77 | Bool | BinaryValue | D341 | 72 |  |  |  | R/W
3 | Set zone 5 (0=Off, 1=On) | Coil | 78 | Bool | BinaryValue | D342 | 73 |  |  |  | R/W
3 | Set zone 6 (0=Off, 1=On) | Coil | 79 | Bool | BinaryValue | D343 | 74 |  |  |  | R/W
3 | Set zone 7 (0=Off, 1=On) | Coil | 80 | Bool | BinaryValue | D344 | 75 |  |  |  | R/W
3 | Set zone 8 (0=Off, 1=On) | Coil | 81 | Bool | BinaryValue | D345 | 76 |  |  |  | R/W
3 | Generic Digital 1 | Coil | 82 | Bool | BinaryValue | D346 | 77 |  |  |  | R/W
3 | Generic Digital 2 | Coil | 83 | Bool | BinaryValue | D347 | 78 |  |  |  | R/W
3 | Generic Digital 3 | Coil | 84 | Bool | BinaryValue | D348 | 79 |  |  |  | R/W
3 | Generic Digital 4 | Coil | 85 | Bool | BinaryValue | D349 | 80 |  |  |  | R/W
3 | Generic Digital 5 | Coil | 86 | Bool | BinaryValue | D350 | 81 |  |  |  | R/W
3 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 184 | Int | IntegerValue | I301 | 610 | 1 | 4 |  | R/W
3 | Set Air Filter Notification Timer | HoldingRegister | 185 | Int | IntegerValue | I302 | 611 | 1 | 10000 | Hours | R/W
3 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 186 | Int | IntegerValue | I303 | 612 | 1 | 4 |  | R/W
3 | Target Airflow | HoldingRegister | 187 | Int | IntegerValue | I304 | 613 | 0 | 6000 | LitersPerSecond | R/W
3 | Enable Volumetric Airflow | HoldingRegister | 188 | Int | IntegerValue | I305 | 614 | 0 | 6000 | LitersPerSecond | R/W
3 | Indoor Pressure Filter level warning | HoldingRegister | 189 | Int | IntegerValue | I306 | 615 | 0 | 6000 | Pascals | R/W
3 | Economiser CO₂ Low Level | HoldingRegister | 190 | Int | IntegerValue | I307 | 616 | 0 | 1000 | PartsPerMillion | R/W
3 | Economiser CO₂ High Level | HoldingRegister | 191 | Int | IntegerValue | I308 | 617 | 0 | 1000 | PartsPerMillion | R/W
3 | BMS card Software version | InputRegister | 184 | Int | IntegerValue | I309 | 974 | 0 | 32767 |  | R
3 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 185 | Int | IntegerValue | I310 | 975 | 0 | 2 |  | R
3 | Air Filter Run Timer | InputRegister | 186 | Int | IntegerValue | I311 | 976 | 0 | 10000 | Hours | R
3 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 187 | Int | IntegerValue | I312 | 977 | 0 | 4 |  | R
3 | Indoor Airflow | InputRegister | 188 | Int | IntegerValue | I313 | 978 | 0 | 6000 | LitersPerSecond | R
3 | Indoor Static Pressure | InputRegister | 189 | Int | IntegerValue | I314 | 979 | 0 | 6000 | Pascals | R
3 | Measured CO₂ level | InputRegister | 190 | Int | IntegerValue | I315 | 980 | 0 | 1000 | PartsPerMillion | R
3 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 191 | Int | IntegerValue | I316 | 981 | 0 | 100 |  | R
3 | Error History Log, 1 error ago | InputRegister | 192 | Int | IntegerValue | I317 | 982 | 0 | 100 |  | R
3 | Error History Log, 2 errors ago | InputRegister | 193 | Int | IntegerValue | I318 | 983 | 0 | 100 |  | R
3 | Error History Log, 3 errors ago | InputRegister | 194 | Int | IntegerValue | I319 | 984 | 0 | 100 |  | R
3 | Error History Log, 4 errors ago | InputRegister | 195 | Int | IntegerValue | I320 | 985 | 0 | 100 |  | R
3 | Error History Log, 5 errors ago | InputRegister | 196 | Int | IntegerValue | I321 | 986 | 0 | 100 |  | R
3 | Outdoor Unit 1 Model | InputRegister | 197 | Int | IntegerValue | I322 | 987 | 0 | 32767 |  | R
3 | Outdoor Unit 1 Software version | InputRegister | 198 | Int | IntegerValue | I323 | 988 | 0 | 32767 |  | R
3 | Compressor 1 Type | InputRegister | 199 | Int | IntegerValue | I324 | 989 | 0 | 100 |  | R
3 | Compressor 1 Suction Pressure | InputRegister | 200 | Int | IntegerValue | I325 | 990 | 0 | 6000 | KiloPascals | R
3 | Compressor 1 Discharge Pressure | InputRegister | 201 | Int | IntegerValue | I326 | 991 | 0 | 6000 | KiloPascals | R
3 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 202 | Int | IntegerValue | I327 | 992 | 0 | 3 |  | R
3 | Indoor Coil 1 Fan 1 Speed | InputRegister | 203 | Int | IntegerValue | I328 | 993 | 0 | 9999 | RevolutionsPerMinute | R
3 | Generic Integer 1 | HoldingRegister | 192 | Int | IntegerValue | I329 | 618 |  |  |  | R/W
3 | Generic Integer 2 | HoldingRegister | 193 | Int | IntegerValue | I330 | 619 |  |  |  | R/W
3 | Generic Integer 3 | HoldingRegister | 194 | Int | IntegerValue | I331 | 620 |  |  |  | R/W
3 | Generic Integer 4 | HoldingRegister | 195 | Int | IntegerValue | I332 | 621 |  |  |  | R/W
3 | Generic Integer 5 | HoldingRegister | 196 | Int | IntegerValue | I333 | 622 |  |  |  | R/W

## Device 4
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
4 | Set Master Setpoint Temperature | HoldingRegister | 210 | Real | AnalogValue | A401 | 623 | 16 | 30 | DegreesCelsius | R/W
4 | Economiser Temperature Difference | HoldingRegister | 214 | Real | AnalogValue | A403 | 625 | 0 | 10 | DegreesCelsius | R/W
4 | Economiser Outside Min Temperature | HoldingRegister | 216 | Real | AnalogValue | A404 | 626 | 0 | 22.5 | DegreesCelsius | R/W
4 | Economiser Outside Max Temperature | HoldingRegister | 218 | Real | AnalogValue | A405 | 627 | 0 | 26 | DegreesCelsius | R/W
4 | Economiser Minimum Damper | HoldingRegister | 220 | Real | AnalogValue | A406 | 628 | 0 | 10 | Volts | R/W
4 | Economiser Maximum Damper | HoldingRegister | 222 | Real | AnalogValue | A407 | 629 | 0 | 10 | Volts | R/W
4 | Economiser Outside Max Moisture | HoldingRegister | 224 | Real | AnalogValue | A408 | 630 | 0 | 100 | GramsPerKilogram | R/W
4 | Economiser Outside Max Dew Point | HoldingRegister | 226 | Real | AnalogValue | A409 | 631 | 0 | 100 | DegreesCelsius | R/W
4 | Economiser Outside Max Enthalpy | HoldingRegister | 228 | Real | AnalogValue | A410 | 632 | 0 | 100 | KilojoulesPerKilogram | R/W
4 | Economiser Enthalpy Delta | HoldingRegister | 230 | Real | AnalogValue | A411 | 633 | 0 | 10 | KilojoulesPerKilogram | R/W
4 | Economiser CO₂ Minimum Damper | HoldingRegister | 232 | Real | AnalogValue | A412 | 634 | 0 | 10 | Volts | R/W
4 | Economiser CO₂ Maximum Damper | HoldingRegister | 234 | Real | AnalogValue | A413 | 635 | 0 | 10 | Volts | R/W
4 | Room Temperature | InputRegister | 212 | Real | AnalogValue | A415 | 995 | -99.9 | 99.9 | DegreesCelsius | R
4 | Indoor Room Temperature | InputRegister | 214 | Real | AnalogValue | A416 | 996 | -99.9 | 99.9 | DegreesCelsius | R
4 | Outside Temperature | InputRegister | 216 | Real | AnalogValue | A417 | 997 | -99.9 | 99.9 | DegreesCelsius | R
4 | Outside Air Temperature | InputRegister | 218 | Real | AnalogValue | A418 | 998 | -99.9 | 99.9 | DegreesCelsius | R
4 | Compressor 1 Suction Temperature | InputRegister | 220 | Real | AnalogValue | A419 | 999 | -999.9 | 999.9 | DegreesCelsius | R
4 | Compressor 1 Discharge Temperature | InputRegister | 222 | Real | AnalogValue | A420 | 1000 | -999.9 | 999.9 | DegreesCelsius | R
4 | Compressor 1 Suction SuperHeat | InputRegister | 224 | Real | AnalogValue | A421 | 1001 | -99.9 | 99.9 | DegreesCelsius | R
4 | Compressor 1 Suction SuperHeat Target | InputRegister | 226 | Real | AnalogValue | A422 | 1002 | -99.9 | 99.9 | DegreesCelsius | R
4 | Outdoor Coil 1 Temperature | InputRegister | 228 | Real | AnalogValue | A423 | 1003 | -99.9 | 99.9 | DegreesCelsius | R
4 | Indoor Coil 1 Temperature | InputRegister | 230 | Real | AnalogValue | A424 | 1004 | -99.9 | 99.9 | DegreesCelsius | R
4 | Wall Control 1 Temperature | InputRegister | 232 | Real | AnalogValue | A425 | 1005 | -99.9 | 99.9 | DegreesCelsius | R
4 | Wall Control 2 Temperature | InputRegister | 234 | Real | AnalogValue | A426 | 1006 | -99.9 | 99.9 | DegreesCelsius | R
4 | Wall Control 3 Temperature | InputRegister | 236 | Real | AnalogValue | A427 | 1007 | -99.9 | 99.9 | DegreesCelsius | R
4 | Auxillary Sensor 1 Temperature | InputRegister | 238 | Real | AnalogValue | A428 | 1008 | -99.9 | 99.9 | DegreesCelsius | R
4 | Auxillary Sensor 2 Temperature | InputRegister | 240 | Real | AnalogValue | A429 | 1009 | -99.9 | 99.9 | DegreesCelsius | R
4 | Auxillary Sensor 3 Temperature | InputRegister | 242 | Real | AnalogValue | A430 | 1010 | -99.9 | 99.9 | DegreesCelsius | R
4 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 236 | Real | AnalogValue | A431 | 636 | 0 | 100 | Percent | R/W
4 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 238 | Real | AnalogValue | A432 | 637 | 0 | 100 | Percent | R/W
4 | Reduced Airflow Speed | HoldingRegister | 240 | Real | AnalogValue | A433 | 638 | 0 | 100 | Percent | R/W
4 | Economiser Outside Max Humidity | HoldingRegister | 242 | Real | AnalogValue | A434 | 639 | 0 | 100 | Percent | R/W
4 | Actual System Running Capacity | InputRegister | 244 | Real | AnalogValue | A435 | 1011 | 0 | 100 | Percent | R
4 | Compressor 1 Demand | InputRegister | 246 | Real | AnalogValue | A436 | 1012 | 0 | 100 | Percent | R
4 | Compressor 1 Speed | InputRegister | 248 | Real | AnalogValue | A437 | 1013 | 0 | 100 | Percent | R
4 | Indoor Coil 1 Fan Speed | InputRegister | 250 | Real | AnalogValue | A438 | 1014 | 0 | 100 | Percent | R
4 | Compressor 1 EEV position | InputRegister | 252 | Real | AnalogValue | A439 | 1015 | 0 | 100 | Percent | R
4 | Generic Analog 01 | HoldingRegister | 244 | Real | AnalogValue | A440 | 640 |  |  |  | R/W
4 | Generic Analog 02 | HoldingRegister | 246 | Real | AnalogValue | A441 | 641 |  |  |  | R/W
4 | Generic Analog 03 | HoldingRegister | 248 | Real | AnalogValue | A442 | 642 |  |  |  | R/W
4 | Generic Analog 04 | HoldingRegister | 250 | Real | AnalogValue | A443 | 643 |  |  |  | R/W
4 | Generic Analog 05 | HoldingRegister | 252 | Real | AnalogValue | A444 | 644 |  |  |  | R/W
4 | Turns the AC Off/On (0=Off, 1=On) | Coil | 90 | Bool | BinaryValue | D401 | 82 |  |  |  | R/W
4 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 91 | Bool | BinaryValue | D402 | 83 |  |  |  | R/W
4 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 92 | Bool | BinaryValue | D403 | 84 |  |  |  | R/W
4 | Set Turbo Mode (0=Off, 1=On) | Coil | 93 | Bool | BinaryValue | D404 | 85 |  |  |  | R/W
4 | Set Quiet Mode (0=Off, 1=On) | Coil | 94 | Bool | BinaryValue | D405 | 86 |  |  |  | R/W
4 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 95 | Bool | BinaryValue | D406 | 87 |  |  |  | R/W
4 | Enable DeSuperHeater (0=Off, 1=On) | Coil | 96 | Bool | BinaryValue | D407 | 88 |  |  |  | R/W
4 | Enable Economiser (0=Off, 1=On) | Coil | 99 | Bool | BinaryValue | D410 | 91 |  |  |  | R/W
4 | Enable Humidity Control | Coil | 100 | Bool | BinaryValue | D411 | 92 |  |  |  | R/W
4 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 101 | Bool | BinaryValue | D412 | 93 |  |  |  | R/W
4 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 102 | Bool | BinaryValue | D413 | 94 |  |  |  | R/W
4 | Enable CO₂ Control (0=Off, 1=On) | Coil | 103 | Bool | BinaryValue | D414 | 95 |  |  |  | R/W
4 | Alarm Output (0=Off, 1=On) | DiscreteInput | 90 | Bool | BinaryValue | D415 | 345 |  |  |  | R
4 | Air Filter Notification | DiscreteInput | 91 | Bool | BinaryValue | D416 | 346 |  |  |  | R
4 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 94 | Bool | BinaryValue | D419 | 349 |  |  |  | R
4 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 95 | Bool | BinaryValue | D420 | 350 |  |  |  | R
4 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 96 | Bool | BinaryValue | D421 | 351 |  |  |  | R
4 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 97 | Bool | BinaryValue | D422 | 352 |  |  |  | R
4 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 98 | Bool | BinaryValue | D423 | 353 |  |  |  | R
4 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 99 | Bool | BinaryValue | D424 | 354 |  |  |  | R
4 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 100 | Bool | BinaryValue | D425 | 355 |  |  |  | R
4 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 101 | Bool | BinaryValue | D426 | 356 |  |  |  | R
4 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 102 | Bool | BinaryValue | D427 | 357 |  |  |  | R
4 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 103 | Bool | BinaryValue | D428 | 358 |  |  |  | R
4 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 104 | Bool | BinaryValue | D429 | 359 |  |  |  | R
4 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 105 | Bool | BinaryValue | D430 | 360 |  |  |  | R
4 | Compressor 1 Discharge Temp High | DiscreteInput | 106 | Bool | BinaryValue | D431 | 361 |  |  |  | R
4 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 107 | Bool | BinaryValue | D432 | 362 |  |  |  | R
4 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 108 | Bool | BinaryValue | D433 | 363 |  |  |  | R
4 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 109 | Bool | BinaryValue | D434 | 364 |  |  |  | R
4 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 110 | Bool | BinaryValue | D435 | 365 |  |  |  | R
4 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 111 | Bool | BinaryValue | D436 | 366 |  |  |  | R
4 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 112 | Bool | BinaryValue | D437 | 367 |  |  |  | R
4 | Set zone 1 (0=Off, 1=On) | Coil | 104 | Bool | BinaryValue | D438 | 96 |  |  |  | R/W
4 | Set zone 2 (0=Off, 1=On) | Coil | 105 | Bool | BinaryValue | D439 | 97 |  |  |  | R/W
4 | Set zone 3 (0=Off, 1=On) | Coil | 106 | Bool | BinaryValue | D440 | 98 |  |  |  | R/W
4 | Set zone 4 (0=Off, 1=On) | Coil | 107 | Bool | BinaryValue | D441 | 99 |  |  |  | R/W
4 | Set zone 5 (0=Off, 1=On) | Coil | 108 | Bool | BinaryValue | D442 | 100 |  |  |  | R/W
4 | Set zone 6 (0=Off, 1=On) | Coil | 109 | Bool | BinaryValue | D443 | 101 |  |  |  | R/W
4 | Set zone 7 (0=Off, 1=On) | Coil | 110 | Bool | BinaryValue | D444 | 102 |  |  |  | R/W
4 | Set zone 8 (0=Off, 1=On) | Coil | 111 | Bool | BinaryValue | D445 | 103 |  |  |  | R/W
4 | Generic Digital 1 | Coil | 112 | Bool | BinaryValue | D446 | 104 |  |  |  | R/W
4 | Generic Digital 2 | Coil | 113 | Bool | BinaryValue | D447 | 105 |  |  |  | R/W
4 | Generic Digital 3 | Coil | 114 | Bool | BinaryValue | D448 | 106 |  |  |  | R/W
4 | Generic Digital 4 | Coil | 115 | Bool | BinaryValue | D449 | 107 |  |  |  | R/W
4 | Generic Digital 5 | Coil | 116 | Bool | BinaryValue | D450 | 108 |  |  |  | R/W
4 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 254 | Int | IntegerValue | I401 | 645 | 1 | 4 |  | R/W
4 | Set Air Filter Notification Timer | HoldingRegister | 255 | Int | IntegerValue | I402 | 646 | 1 | 10000 | Hours | R/W
4 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 256 | Int | IntegerValue | I403 | 647 | 1 | 4 |  | R/W
4 | Target Airflow | HoldingRegister | 257 | Int | IntegerValue | I404 | 648 | 0 | 6000 | LitersPerSecond | R/W
4 | Enable Volumetric Airflow | HoldingRegister | 258 | Int | IntegerValue | I405 | 649 | 0 | 6000 | LitersPerSecond | R/W
4 | Indoor Pressure Filter level warning | HoldingRegister | 259 | Int | IntegerValue | I406 | 650 | 0 | 6000 | Pascals | R/W
4 | Economiser CO₂ Low Level | HoldingRegister | 260 | Int | IntegerValue | I407 | 651 | 0 | 1000 | PartsPerMillion | R/W
4 | Economiser CO₂ High Level | HoldingRegister | 261 | Int | IntegerValue | I408 | 652 | 0 | 1000 | PartsPerMillion | R/W
4 | BMS card Software version | InputRegister | 254 | Int | IntegerValue | I409 | 1016 | 0 | 32767 |  | R
4 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 255 | Int | IntegerValue | I410 | 1017 | 0 | 2 |  | R
4 | Air Filter Run Timer | InputRegister | 256 | Int | IntegerValue | I411 | 1018 | 0 | 10000 | Hours | R
4 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 257 | Int | IntegerValue | I412 | 1019 | 0 | 4 |  | R
4 | Indoor Airflow | InputRegister | 258 | Int | IntegerValue | I413 | 1020 | 0 | 6000 | LitersPerSecond | R
4 | Indoor Static Pressure | InputRegister | 259 | Int | IntegerValue | I414 | 1021 | 0 | 6000 | Pascals | R
4 | Measured CO₂ level | InputRegister | 260 | Int | IntegerValue | I415 | 1022 | 0 | 1000 | PartsPerMillion | R
4 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 261 | Int | IntegerValue | I416 | 1023 | 0 | 100 |  | R
4 | Error History Log, 1 error ago | InputRegister | 262 | Int | IntegerValue | I417 | 1024 | 0 | 100 |  | R
4 | Error History Log, 2 errors ago | InputRegister | 263 | Int | IntegerValue | I418 | 1025 | 0 | 100 |  | R
4 | Error History Log, 3 errors ago | InputRegister | 264 | Int | IntegerValue | I419 | 1026 | 0 | 100 |  | R
4 | Error History Log, 4 errors ago | InputRegister | 265 | Int | IntegerValue | I420 | 1027 | 0 | 100 |  | R
4 | Error History Log, 5 errors ago | InputRegister | 266 | Int | IntegerValue | I421 | 1028 | 0 | 100 |  | R
4 | Outdoor Unit 1 Model | InputRegister | 267 | Int | IntegerValue | I422 | 1029 | 0 | 32767 |  | R
4 | Outdoor Unit 1 Software version | InputRegister | 268 | Int | IntegerValue | I423 | 1030 | 0 | 32767 |  | R
4 | Compressor 1 Type | InputRegister | 269 | Int | IntegerValue | I424 | 1031 | 0 | 100 |  | R
4 | Compressor 1 Suction Pressure | InputRegister | 270 | Int | IntegerValue | I425 | 1032 | 0 | 6000 | KiloPascals | R
4 | Compressor 1 Discharge Pressure | InputRegister | 271 | Int | IntegerValue | I426 | 1033 | 0 | 6000 | KiloPascals | R
4 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 272 | Int | IntegerValue | I427 | 1034 | 0 | 3 |  | R
4 | Indoor Coil 1 Fan 1 Speed | InputRegister | 273 | Int | IntegerValue | I428 | 1035 | 0 | 9999 | RevolutionsPerMinute | R
4 | Generic Integer 1 | HoldingRegister | 262 | Int | IntegerValue | I429 | 653 |  |  |  | R/W
4 | Generic Integer 2 | HoldingRegister | 263 | Int | IntegerValue | I430 | 654 |  |  |  | R/W
4 | Generic Integer 3 | HoldingRegister | 264 | Int | IntegerValue | I431 | 655 |  |  |  | R/W
4 | Generic Integer 4 | HoldingRegister | 265 | Int | IntegerValue | I432 | 656 |  |  |  | R/W
4 | Generic Integer 5 | HoldingRegister | 266 | Int | IntegerValue | I433 | 657 |  |  |  | R/W

## Device 5
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
5 | Set Master Setpoint Temperature | HoldingRegister | 280 | Real | AnalogValue | A501 | 658 | 16 | 30 | DegreesCelsius | R/W
5 | Economiser Temperature Difference | HoldingRegister | 284 | Real | AnalogValue | A503 | 660 | 0 | 10 | DegreesCelsius | R/W
5 | Economiser Outside Min Temperature | HoldingRegister | 286 | Real | AnalogValue | A504 | 661 | 0 | 22.5 | DegreesCelsius | R/W
5 | Economiser Outside Max Temperature | HoldingRegister | 288 | Real | AnalogValue | A505 | 662 | 0 | 26 | DegreesCelsius | R/W
5 | Economiser Minimum Damper | HoldingRegister | 290 | Real | AnalogValue | A506 | 663 | 0 | 10 | Volts | R/W
5 | Economiser Maximum Damper | HoldingRegister | 292 | Real | AnalogValue | A507 | 664 | 0 | 10 | Volts | R/W
5 | Economiser Outside Max Moisture | HoldingRegister | 294 | Real | AnalogValue | A508 | 665 | 0 | 100 | GramsPerKilogram | R/W
5 | Economiser Outside Max Dew Point | HoldingRegister | 296 | Real | AnalogValue | A509 | 666 | 0 | 100 | DegreesCelsius | R/W
5 | Economiser Outside Max Enthalpy | HoldingRegister | 298 | Real | AnalogValue | A510 | 667 | 0 | 100 | KilojoulesPerKilogram | R/W
5 | Economiser Enthalpy Delta | HoldingRegister | 300 | Real | AnalogValue | A511 | 668 | 0 | 10 | KilojoulesPerKilogram | R/W
5 | Economiser CO₂ Minimum Damper | HoldingRegister | 302 | Real | AnalogValue | A512 | 669 | 0 | 10 | Volts | R/W
5 | Economiser CO₂ Maximum Damper | HoldingRegister | 304 | Real | AnalogValue | A513 | 670 | 0 | 10 | Volts | R/W
5 | Room Temperature | InputRegister | 282 | Real | AnalogValue | A515 | 1037 | -99.9 | 99.9 | DegreesCelsius | R
5 | Indoor Room Temperature | InputRegister | 284 | Real | AnalogValue | A516 | 1038 | -99.9 | 99.9 | DegreesCelsius | R
5 | Outside Temperature | InputRegister | 286 | Real | AnalogValue | A517 | 1039 | -99.9 | 99.9 | DegreesCelsius | R
5 | Outside Air Temperature | InputRegister | 288 | Real | AnalogValue | A518 | 1040 | -99.9 | 99.9 | DegreesCelsius | R
5 | Compressor 1 Suction Temperature | InputRegister | 290 | Real | AnalogValue | A519 | 1041 | -999.9 | 999.9 | DegreesCelsius | R
5 | Compressor 1 Discharge Temperature | InputRegister | 292 | Real | AnalogValue | A520 | 1042 | -999.9 | 999.9 | DegreesCelsius | R
5 | Compressor 1 Suction SuperHeat | InputRegister | 294 | Real | AnalogValue | A521 | 1043 | -99.9 | 99.9 | DegreesCelsius | R
5 | Compressor 1 Suction SuperHeat Target | InputRegister | 296 | Real | AnalogValue | A522 | 1044 | -99.9 | 99.9 | DegreesCelsius | R
5 | Outdoor Coil 1 Temperature | InputRegister | 298 | Real | AnalogValue | A523 | 1045 | -99.9 | 99.9 | DegreesCelsius | R
5 | Indoor Coil 1 Temperature | InputRegister | 300 | Real | AnalogValue | A524 | 1046 | -99.9 | 99.9 | DegreesCelsius | R
5 | Wall Control 1 Temperature | InputRegister | 302 | Real | AnalogValue | A525 | 1047 | -99.9 | 99.9 | DegreesCelsius | R
5 | Wall Control 2 Temperature | InputRegister | 304 | Real | AnalogValue | A526 | 1048 | -99.9 | 99.9 | DegreesCelsius | R
5 | Wall Control 3 Temperature | InputRegister | 306 | Real | AnalogValue | A527 | 1049 | -99.9 | 99.9 | DegreesCelsius | R
5 | Auxillary Sensor 1 Temperature | InputRegister | 308 | Real | AnalogValue | A528 | 1050 | -99.9 | 99.9 | DegreesCelsius | R
5 | Auxillary Sensor 2 Temperature | InputRegister | 310 | Real | AnalogValue | A529 | 1051 | -99.9 | 99.9 | DegreesCelsius | R
5 | Auxillary Sensor 3 Temperature | InputRegister | 312 | Real | AnalogValue | A530 | 1052 | -99.9 | 99.9 | DegreesCelsius | R
5 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 306 | Real | AnalogValue | A531 | 671 | 0 | 100 | Percent | R/W
5 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 308 | Real | AnalogValue | A532 | 672 | 0 | 100 | Percent | R/W
5 | Reduced Airflow Speed | HoldingRegister | 310 | Real | AnalogValue | A533 | 673 | 0 | 100 | Percent | R/W
5 | Economiser Outside Max Humidity | HoldingRegister | 312 | Real | AnalogValue | A534 | 674 | 0 | 100 | Percent | R/W
5 | Actual System Running Capacity | InputRegister | 314 | Real | AnalogValue | A535 | 1053 | 0 | 100 | Percent | R
5 | Compressor 1 Demand | InputRegister | 316 | Real | AnalogValue | A536 | 1054 | 0 | 100 | Percent | R
5 | Compressor 1 Speed | InputRegister | 318 | Real | AnalogValue | A537 | 1055 | 0 | 100 | Percent | R
5 | Indoor Coil 1 Fan Speed | InputRegister | 320 | Real | AnalogValue | A538 | 1056 | 0 | 100 | Percent | R
5 | Compressor 1 EEV position | InputRegister | 322 | Real | AnalogValue | A539 | 1057 | 0 | 100 | Percent | R
5 | Generic Analog 01 | HoldingRegister | 314 | Real | AnalogValue | A540 | 675 |  |  |  | R/W
5 | Generic Analog 02 | HoldingRegister | 316 | Real | AnalogValue | A541 | 676 |  |  |  | R/W
5 | Generic Analog 03 | HoldingRegister | 318 | Real | AnalogValue | A542 | 677 |  |  |  | R/W
5 | Generic Analog 04 | HoldingRegister | 320 | Real | AnalogValue | A543 | 678 |  |  |  | R/W
5 | Generic Analog 05 | HoldingRegister | 322 | Real | AnalogValue | A544 | 679 |  |  |  | R/W
5 | Turns the AC Off/On (0=Off, 1=On) | Coil | 120 | Bool | BinaryValue | D501 | 109 |  |  |  | R/W
5 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 121 | Bool | BinaryValue | D502 | 110 |  |  |  | R/W
5 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 122 | Bool | BinaryValue | D503 | 111 |  |  |  | R/W
5 | Set Turbo Mode (0=Off, 1=On) | Coil | 123 | Bool | BinaryValue | D504 | 112 |  |  |  | R/W
5 | Set Quiet Mode (0=Off, 1=On) | Coil | 124 | Bool | BinaryValue | D505 | 113 |  |  |  | R/W
5 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 125 | Bool | BinaryValue | D506 | 114 |  |  |  | R/W
5 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 128 | Bool | BinaryValue | D509 | 117 |  |  |  | R/W
5 | Enable Economiser (0=Off, 1=On) | Coil | 129 | Bool | BinaryValue | D510 | 118 |  |  |  | R/W
5 | Enable Humidity Control | Coil | 130 | Bool | BinaryValue | D511 | 119 |  |  |  | R/W
5 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 131 | Bool | BinaryValue | D512 | 120 |  |  |  | R/W
5 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 132 | Bool | BinaryValue | D513 | 121 |  |  |  | R/W
5 | Enable CO₂ Control (0=Off, 1=On) | Coil | 133 | Bool | BinaryValue | D514 | 122 |  |  |  | R/W
5 | Alarm Output (0=Off, 1=On) | DiscreteInput | 120 | Bool | BinaryValue | D515 | 368 |  |  |  | R
5 | Air Filter Notification | DiscreteInput | 121 | Bool | BinaryValue | D516 | 369 |  |  |  | R
5 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 124 | Bool | BinaryValue | D519 | 372 |  |  |  | R
5 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 125 | Bool | BinaryValue | D520 | 373 |  |  |  | R
5 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 126 | Bool | BinaryValue | D521 | 374 |  |  |  | R
5 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 127 | Bool | BinaryValue | D522 | 375 |  |  |  | R
5 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 128 | Bool | BinaryValue | D523 | 376 |  |  |  | R
5 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 129 | Bool | BinaryValue | D524 | 377 |  |  |  | R
5 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 130 | Bool | BinaryValue | D525 | 378 |  |  |  | R
5 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 131 | Bool | BinaryValue | D526 | 379 |  |  |  | R
5 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 132 | Bool | BinaryValue | D527 | 380 |  |  |  | R
5 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 133 | Bool | BinaryValue | D528 | 381 |  |  |  | R
5 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 134 | Bool | BinaryValue | D529 | 382 |  |  |  | R
5 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 135 | Bool | BinaryValue | D530 | 383 |  |  |  | R
5 | Compressor 1 Discharge Temp High | DiscreteInput | 136 | Bool | BinaryValue | D531 | 384 |  |  |  | R
5 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 137 | Bool | BinaryValue | D532 | 385 |  |  |  | R
5 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 138 | Bool | BinaryValue | D533 | 386 |  |  |  | R
5 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 139 | Bool | BinaryValue | D534 | 387 |  |  |  | R
5 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 140 | Bool | BinaryValue | D535 | 388 |  |  |  | R
5 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 141 | Bool | BinaryValue | D536 | 389 |  |  |  | R
5 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 142 | Bool | BinaryValue | D537 | 390 |  |  |  | R
5 | Set zone 1 (0=Off, 1=On) | Coil | 134 | Bool | BinaryValue | D538 | 123 |  |  |  | R/W
5 | Set zone 2 (0=Off, 1=On) | Coil | 135 | Bool | BinaryValue | D539 | 124 |  |  |  | R/W
5 | Set zone 3 (0=Off, 1=On) | Coil | 136 | Bool | BinaryValue | D540 | 125 |  |  |  | R/W
5 | Set zone 4 (0=Off, 1=On) | Coil | 137 | Bool | BinaryValue | D541 | 126 |  |  |  | R/W
5 | Set zone 5 (0=Off, 1=On) | Coil | 138 | Bool | BinaryValue | D542 | 127 |  |  |  | R/W
5 | Set zone 6 (0=Off, 1=On) | Coil | 139 | Bool | BinaryValue | D543 | 128 |  |  |  | R/W
5 | Set zone 7 (0=Off, 1=On) | Coil | 140 | Bool | BinaryValue | D544 | 129 |  |  |  | R/W
5 | Set zone 8 (0=Off, 1=On) | Coil | 141 | Bool | BinaryValue | D545 | 130 |  |  |  | R/W
5 | Generic Digital 1 | Coil | 142 | Bool | BinaryValue | D546 | 131 |  |  |  | R/W
5 | Generic Digital 2 | Coil | 143 | Bool | BinaryValue | D547 | 132 |  |  |  | R/W
5 | Generic Digital 3 | Coil | 144 | Bool | BinaryValue | D548 | 133 |  |  |  | R/W
5 | Generic Digital 4 | Coil | 145 | Bool | BinaryValue | D549 | 134 |  |  |  | R/W
5 | Generic Digital 5 | Coil | 146 | Bool | BinaryValue | D550 | 135 |  |  |  | R/W
5 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 324 | Int | IntegerValue | I501 | 680 | 1 | 4 |  | R/W
5 | Set Air Filter Notification Timer | HoldingRegister | 325 | Int | IntegerValue | I502 | 681 | 1 | 10000 | Hours | R/W
5 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 326 | Int | IntegerValue | I503 | 682 | 1 | 4 |  | R/W
5 | Target Airflow | HoldingRegister | 327 | Int | IntegerValue | I504 | 683 | 0 | 6000 | LitersPerSecond | R/W
5 | Enable Volumetric Airflow | HoldingRegister | 328 | Int | IntegerValue | I505 | 684 | 0 | 6000 | LitersPerSecond | R/W
5 | Indoor Pressure Filter level warning | HoldingRegister | 329 | Int | IntegerValue | I506 | 685 | 0 | 6000 | Pascals | R/W
5 | Economiser CO₂ Low Level | HoldingRegister | 330 | Int | IntegerValue | I507 | 686 | 0 | 1000 | PartsPerMillion | R/W
5 | Economiser CO₂ High Level | HoldingRegister | 331 | Int | IntegerValue | I508 | 687 | 0 | 1000 | PartsPerMillion | R/W
5 | BMS card Software version | InputRegister | 324 | Int | IntegerValue | I509 | 1058 | 0 | 32767 |  | R
5 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 325 | Int | IntegerValue | I510 | 1059 | 0 | 2 |  | R
5 | Air Filter Run Timer | InputRegister | 326 | Int | IntegerValue | I511 | 1060 | 0 | 10000 | Hours | R
5 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 327 | Int | IntegerValue | I512 | 1061 | 0 | 4 |  | R
5 | Indoor Airflow | InputRegister | 328 | Int | IntegerValue | I513 | 1062 | 0 | 6000 | LitersPerSecond | R
5 | Indoor Static Pressure | InputRegister | 329 | Int | IntegerValue | I514 | 1063 | 0 | 6000 | Pascals | R
5 | Measured CO₂ level | InputRegister | 330 | Int | IntegerValue | I515 | 1064 | 0 | 1000 | PartsPerMillion | R
5 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 331 | Int | IntegerValue | I516 | 1065 | 0 | 100 |  | R
5 | Error History Log, 1 error ago | InputRegister | 332 | Int | IntegerValue | I517 | 1066 | 0 | 100 |  | R
5 | Error History Log, 2 errors ago | InputRegister | 333 | Int | IntegerValue | I518 | 1067 | 0 | 100 |  | R
5 | Error History Log, 3 errors ago | InputRegister | 334 | Int | IntegerValue | I519 | 1068 | 0 | 100 |  | R
5 | Error History Log, 4 errors ago | InputRegister | 335 | Int | IntegerValue | I520 | 1069 | 0 | 100 |  | R
5 | Error History Log, 5 errors ago | InputRegister | 336 | Int | IntegerValue | I521 | 1070 | 0 | 100 |  | R
5 | Outdoor Unit 1 Model | InputRegister | 337 | Int | IntegerValue | I522 | 1071 | 0 | 32767 |  | R
5 | Outdoor Unit 1 Software version | InputRegister | 338 | Int | IntegerValue | I523 | 1072 | 0 | 32767 |  | R
5 | Compressor 1 Type | InputRegister | 339 | Int | IntegerValue | I524 | 1073 | 0 | 100 |  | R
5 | Compressor 1 Suction Pressure | InputRegister | 340 | Int | IntegerValue | I525 | 1074 | 0 | 6000 | KiloPascals | R
5 | Compressor 1 Discharge Pressure | InputRegister | 341 | Int | IntegerValue | I526 | 1075 | 0 | 6000 | KiloPascals | R
5 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 342 | Int | IntegerValue | I527 | 1076 | 0 | 3 |  | R
5 | Indoor Coil 1 Fan 1 Speed | InputRegister | 343 | Int | IntegerValue | I528 | 1077 | 0 | 9999 | RevolutionsPerMinute | R
5 | Generic Integer 1 | HoldingRegister | 332 | Int | IntegerValue | I529 | 688 |  |  |  | R/W
5 | Generic Integer 2 | HoldingRegister | 333 | Int | IntegerValue | I530 | 689 |  |  |  | R/W
5 | Generic Integer 3 | HoldingRegister | 334 | Int | IntegerValue | I531 | 690 |  |  |  | R/W
5 | Generic Integer 4 | HoldingRegister | 335 | Int | IntegerValue | I532 | 691 |  |  |  | R/W
5 | Generic Integer 5 | HoldingRegister | 336 | Int | IntegerValue | I533 | 692 |  |  |  | R/W

## Device 6
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
6 | Set Master Setpoint Temperature | HoldingRegister | 350 | Real | AnalogValue | A601 | 693 | 16 | 30 | DegreesCelsius | R/W
6 | Economiser Temperature Difference | HoldingRegister | 354 | Real | AnalogValue | A603 | 695 | 0 | 10 | DegreesCelsius | R/W
6 | Economiser Outside Min Temperature | HoldingRegister | 356 | Real | AnalogValue | A604 | 696 | 0 | 22.5 | DegreesCelsius | R/W
6 | Economiser Outside Max Temperature | HoldingRegister | 358 | Real | AnalogValue | A605 | 697 | 0 | 26 | DegreesCelsius | R/W
6 | Economiser Minimum Damper | HoldingRegister | 360 | Real | AnalogValue | A606 | 698 | 0 | 10 | Volts | R/W
6 | Economiser Maximum Damper | HoldingRegister | 362 | Real | AnalogValue | A607 | 699 | 0 | 10 | Volts | R/W
6 | Economiser Outside Max Moisture | HoldingRegister | 364 | Real | AnalogValue | A608 | 700 | 0 | 100 | GramsPerKilogram | R/W
6 | Economiser Outside Max Dew Point | HoldingRegister | 366 | Real | AnalogValue | A609 | 701 | 0 | 100 | DegreesCelsius | R/W
6 | Economiser Outside Max Enthalpy | HoldingRegister | 368 | Real | AnalogValue | A610 | 702 | 0 | 100 | KilojoulesPerKilogram | R/W
6 | Economiser Enthalpy Delta | HoldingRegister | 370 | Real | AnalogValue | A611 | 703 | 0 | 10 | KilojoulesPerKilogram | R/W
6 | Economiser CO₂ Minimum Damper | HoldingRegister | 372 | Real | AnalogValue | A612 | 704 | 0 | 10 | Volts | R/W
6 | Economiser CO₂ Maximum Damper | HoldingRegister | 374 | Real | AnalogValue | A613 | 705 | 0 | 10 | Volts | R/W
6 | Room Temperature | InputRegister | 352 | Real | AnalogValue | A615 | 1079 | -99.9 | 99.9 | DegreesCelsius | R
6 | Indoor Room Temperature | InputRegister | 354 | Real | AnalogValue | A616 | 1080 | -99.9 | 99.9 | DegreesCelsius | R
6 | Outside Temperature | InputRegister | 356 | Real | AnalogValue | A617 | 1081 | -99.9 | 99.9 | DegreesCelsius | R
6 | Outside Air Temperature | InputRegister | 358 | Real | AnalogValue | A618 | 1082 | -99.9 | 99.9 | DegreesCelsius | R
6 | Compressor 1 Suction Temperature | InputRegister | 360 | Real | AnalogValue | A619 | 1083 | -999.9 | 999.9 | DegreesCelsius | R
6 | Compressor 1 Discharge Temperature | InputRegister | 362 | Real | AnalogValue | A620 | 1084 | -999.9 | 999.9 | DegreesCelsius | R
6 | Compressor 1 Suction SuperHeat | InputRegister | 364 | Real | AnalogValue | A621 | 1085 | -99.9 | 99.9 | DegreesCelsius | R
6 | Compressor 1 Suction SuperHeat Target | InputRegister | 366 | Real | AnalogValue | A622 | 1086 | -99.9 | 99.9 | DegreesCelsius | R
6 | Outdoor Coil 1 Temperature | InputRegister | 368 | Real | AnalogValue | A623 | 1087 | -99.9 | 99.9 | DegreesCelsius | R
6 | Indoor Coil 1 Temperature | InputRegister | 370 | Real | AnalogValue | A624 | 1088 | -99.9 | 99.9 | DegreesCelsius | R
6 | Wall Control 1 Temperature | InputRegister | 372 | Real | AnalogValue | A625 | 1089 | -99.9 | 99.9 | DegreesCelsius | R
6 | Wall Control 2 Temperature | InputRegister | 374 | Real | AnalogValue | A626 | 1090 | -99.9 | 99.9 | DegreesCelsius | R
6 | Wall Control 3 Temperature | InputRegister | 376 | Real | AnalogValue | A627 | 1091 | -99.9 | 99.9 | DegreesCelsius | R
6 | Auxillary Sensor 1 Temperature | InputRegister | 378 | Real | AnalogValue | A628 | 1092 | -99.9 | 99.9 | DegreesCelsius | R
6 | Auxillary Sensor 2 Temperature | InputRegister | 380 | Real | AnalogValue | A629 | 1093 | -99.9 | 99.9 | DegreesCelsius | R
6 | Auxillary Sensor 3 Temperature | InputRegister | 382 | Real | AnalogValue | A630 | 1094 | -99.9 | 99.9 | DegreesCelsius | R
6 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 376 | Real | AnalogValue | A631 | 706 | 0 | 100 | Percent | R/W
6 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 378 | Real | AnalogValue | A632 | 707 | 0 | 100 | Percent | R/W
6 | Reduced Airflow Speed | HoldingRegister | 380 | Real | AnalogValue | A633 | 708 | 0 | 100 | Percent | R/W
6 | Economiser Outside Max Humidity | HoldingRegister | 382 | Real | AnalogValue | A634 | 709 | 0 | 100 | Percent | R/W
6 | Actual System Running Capacity | InputRegister | 384 | Real | AnalogValue | A635 | 1095 | 0 | 100 | Percent | R
6 | Compressor 1 Demand | InputRegister | 386 | Real | AnalogValue | A636 | 1096 | 0 | 100 | Percent | R
6 | Compressor 1 Speed | InputRegister | 388 | Real | AnalogValue | A637 | 1097 | 0 | 100 | Percent | R
6 | Indoor Coil 1 Fan Speed | InputRegister | 390 | Real | AnalogValue | A638 | 1098 | 0 | 100 | Percent | R
6 | Compressor 1 EEV position | InputRegister | 392 | Real | AnalogValue | A639 | 1099 | 0 | 100 | Percent | R
6 | Generic Analog 01 | HoldingRegister | 384 | Real | AnalogValue | A640 | 710 |  |  |  | R/W
6 | Generic Analog 02 | HoldingRegister | 386 | Real | AnalogValue | A641 | 711 |  |  |  | R/W
6 | Generic Analog 03 | HoldingRegister | 388 | Real | AnalogValue | A642 | 712 |  |  |  | R/W
6 | Generic Analog 04 | HoldingRegister | 390 | Real | AnalogValue | A643 | 713 |  |  |  | R/W
6 | Generic Analog 05 | HoldingRegister | 392 | Real | AnalogValue | A644 | 714 |  |  |  | R/W
6 | Turns the AC Off/On (0=Off, 1=On) | Coil | 150 | Bool | BinaryValue | D601 | 136 |  |  |  | R/W
6 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 151 | Bool | BinaryValue | D602 | 137 |  |  |  | R/W
6 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 152 | Bool | BinaryValue | D603 | 138 |  |  |  | R/W
6 | Set Turbo Mode (0=Off, 1=On) | Coil | 153 | Bool | BinaryValue | D604 | 139 |  |  |  | R/W
6 | Set Quiet Mode (0=Off, 1=On) | Coil | 154 | Bool | BinaryValue | D605 | 140 |  |  |  | R/W
6 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 155 | Bool | BinaryValue | D606 | 141 |  |  |  | R/W
6 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 158 | Bool | BinaryValue | D609 | 144 |  |  |  | R/W
6 | Enable Economiser (0=Off, 1=On) | Coil | 159 | Bool | BinaryValue | D610 | 145 |  |  |  | R/W
6 | Enable Humidity Control | Coil | 160 | Bool | BinaryValue | D611 | 146 |  |  |  | R/W
6 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 161 | Bool | BinaryValue | D612 | 147 |  |  |  | R/W
6 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 162 | Bool | BinaryValue | D613 | 148 |  |  |  | R/W
6 | Enable CO₂ Control (0=Off, 1=On) | Coil | 163 | Bool | BinaryValue | D614 | 149 |  |  |  | R/W
6 | Alarm Output (0=Off, 1=On) | DiscreteInput | 150 | Bool | BinaryValue | D615 | 391 |  |  |  | R
6 | Air Filter Notification | DiscreteInput | 151 | Bool | BinaryValue | D616 | 392 |  |  |  | R
6 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 154 | Bool | BinaryValue | D619 | 395 |  |  |  | R
6 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 155 | Bool | BinaryValue | D620 | 396 |  |  |  | R
6 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 156 | Bool | BinaryValue | D621 | 397 |  |  |  | R
6 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 157 | Bool | BinaryValue | D622 | 398 |  |  |  | R
6 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 158 | Bool | BinaryValue | D623 | 399 |  |  |  | R
6 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 159 | Bool | BinaryValue | D624 | 400 |  |  |  | R
6 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 160 | Bool | BinaryValue | D625 | 401 |  |  |  | R
6 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 161 | Bool | BinaryValue | D626 | 402 |  |  |  | R
6 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 162 | Bool | BinaryValue | D627 | 403 |  |  |  | R
6 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 163 | Bool | BinaryValue | D628 | 404 |  |  |  | R
6 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 164 | Bool | BinaryValue | D629 | 405 |  |  |  | R
6 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 165 | Bool | BinaryValue | D630 | 406 |  |  |  | R
6 | Compressor 1 Discharge Temp High | DiscreteInput | 166 | Bool | BinaryValue | D631 | 407 |  |  |  | R
6 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 167 | Bool | BinaryValue | D632 | 408 |  |  |  | R
6 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 168 | Bool | BinaryValue | D633 | 409 |  |  |  | R
6 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 169 | Bool | BinaryValue | D634 | 410 |  |  |  | R
6 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 170 | Bool | BinaryValue | D635 | 411 |  |  |  | R
6 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 171 | Bool | BinaryValue | D636 | 412 |  |  |  | R
6 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 172 | Bool | BinaryValue | D637 | 413 |  |  |  | R
6 | Set zone 1 (0=Off, 1=On) | Coil | 164 | Bool | BinaryValue | D638 | 150 |  |  |  | R/W
6 | Set zone 2 (0=Off, 1=On) | Coil | 165 | Bool | BinaryValue | D639 | 151 |  |  |  | R/W
6 | Set zone 3 (0=Off, 1=On) | Coil | 166 | Bool | BinaryValue | D640 | 152 |  |  |  | R/W
6 | Set zone 4 (0=Off, 1=On) | Coil | 167 | Bool | BinaryValue | D641 | 153 |  |  |  | R/W
6 | Set zone 5 (0=Off, 1=On) | Coil | 168 | Bool | BinaryValue | D642 | 154 |  |  |  | R/W
6 | Set zone 6 (0=Off, 1=On) | Coil | 169 | Bool | BinaryValue | D643 | 155 |  |  |  | R/W
6 | Set zone 7 (0=Off, 1=On) | Coil | 170 | Bool | BinaryValue | D644 | 156 |  |  |  | R/W
6 | Set zone 8 (0=Off, 1=On) | Coil | 171 | Bool | BinaryValue | D645 | 157 |  |  |  | R/W
6 | Generic Digital 1 | Coil | 172 | Bool | BinaryValue | D646 | 158 |  |  |  | R/W
6 | Generic Digital 2 | Coil | 173 | Bool | BinaryValue | D647 | 159 |  |  |  | R/W
6 | Generic Digital 3 | Coil | 174 | Bool | BinaryValue | D648 | 160 |  |  |  | R/W
6 | Generic Digital 4 | Coil | 175 | Bool | BinaryValue | D649 | 161 |  |  |  | R/W
6 | Generic Digital 5 | Coil | 176 | Bool | BinaryValue | D650 | 162 |  |  |  | R/W
6 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 394 | Int | IntegerValue | I601 | 715 | 1 | 4 |  | R/W
6 | Set Air Filter Notification Timer | HoldingRegister | 395 | Int | IntegerValue | I602 | 716 | 1 | 10000 | Hours | R/W
6 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 396 | Int | IntegerValue | I603 | 717 | 1 | 4 |  | R/W
6 | Target Airflow | HoldingRegister | 397 | Int | IntegerValue | I604 | 718 | 0 | 6000 | LitersPerSecond | R/W
6 | Enable Volumetric Airflow | HoldingRegister | 398 | Int | IntegerValue | I605 | 719 | 0 | 6000 | LitersPerSecond | R/W
6 | Indoor Pressure Filter level warning | HoldingRegister | 399 | Int | IntegerValue | I606 | 720 | 0 | 6000 | Pascals | R/W
6 | Economiser CO₂ Low Level | HoldingRegister | 400 | Int | IntegerValue | I607 | 721 | 0 | 1000 | PartsPerMillion | R/W
6 | Economiser CO₂ High Level | HoldingRegister | 401 | Int | IntegerValue | I608 | 722 | 0 | 1000 | PartsPerMillion | R/W
6 | BMS card Software version | InputRegister | 394 | Int | IntegerValue | I609 | 1100 | 0 | 32767 |  | R
6 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 395 | Int | IntegerValue | I610 | 1101 | 0 | 2 |  | R
6 | Air Filter Run Timer | InputRegister | 396 | Int | IntegerValue | I611 | 1102 | 0 | 10000 | Hours | R
6 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 397 | Int | IntegerValue | I612 | 1103 | 0 | 4 |  | R
6 | Indoor Airflow | InputRegister | 398 | Int | IntegerValue | I613 | 1104 | 0 | 6000 | LitersPerSecond | R
6 | Indoor Static Pressure | InputRegister | 399 | Int | IntegerValue | I614 | 1105 | 0 | 6000 | Pascals | R
6 | Measured CO₂ level | InputRegister | 400 | Int | IntegerValue | I615 | 1106 | 0 | 1000 | PartsPerMillion | R
6 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 401 | Int | IntegerValue | I616 | 1107 | 0 | 100 |  | R
6 | Error History Log, 1 error ago | InputRegister | 402 | Int | IntegerValue | I617 | 1108 | 0 | 100 |  | R
6 | Error History Log, 2 errors ago | InputRegister | 403 | Int | IntegerValue | I618 | 1109 | 0 | 100 |  | R
6 | Error History Log, 3 errors ago | InputRegister | 404 | Int | IntegerValue | I619 | 1110 | 0 | 100 |  | R
6 | Error History Log, 4 errors ago | InputRegister | 405 | Int | IntegerValue | I620 | 1111 | 0 | 100 |  | R
6 | Error History Log, 5 errors ago | InputRegister | 406 | Int | IntegerValue | I621 | 1112 | 0 | 100 |  | R
6 | Outdoor Unit 1 Model | InputRegister | 407 | Int | IntegerValue | I622 | 1113 | 0 | 32767 |  | R
6 | Outdoor Unit 1 Software version | InputRegister | 408 | Int | IntegerValue | I623 | 1114 | 0 | 32767 |  | R
6 | Compressor 1 Type | InputRegister | 409 | Int | IntegerValue | I624 | 1115 | 0 | 100 |  | R
6 | Compressor 1 Suction Pressure | InputRegister | 410 | Int | IntegerValue | I625 | 1116 | 0 | 6000 | KiloPascals | R
6 | Compressor 1 Discharge Pressure | InputRegister | 411 | Int | IntegerValue | I626 | 1117 | 0 | 6000 | KiloPascals | R
6 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 412 | Int | IntegerValue | I627 | 1118 | 0 | 3 |  | R
6 | Indoor Coil 1 Fan 1 Speed | InputRegister | 413 | Int | IntegerValue | I628 | 1119 | 0 | 9999 | RevolutionsPerMinute | R
6 | Generic Integer 1 | HoldingRegister | 402 | Int | IntegerValue | I629 | 723 |  |  |  | R/W
6 | Generic Integer 2 | HoldingRegister | 403 | Int | IntegerValue | I630 | 724 |  |  |  | R/W
6 | Generic Integer 3 | HoldingRegister | 404 | Int | IntegerValue | I631 | 725 |  |  |  | R/W
6 | Generic Integer 4 | HoldingRegister | 405 | Int | IntegerValue | I632 | 726 |  |  |  | R/W
6 | Generic Integer 5 | HoldingRegister | 406 | Int | IntegerValue | I633 | 727 |  |  |  | R/W

## Device 7
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
7 | Set Master Setpoint Temperature | HoldingRegister | 420 | Real | AnalogValue | A701 | 728 | 16 | 30 | DegreesCelsius | R/W
7 | Economiser Temperature Difference | HoldingRegister | 424 | Real | AnalogValue | A703 | 730 | 0 | 10 | DegreesCelsius | R/W
7 | Economiser Outside Min Temperature | HoldingRegister | 426 | Real | AnalogValue | A704 | 731 | 0 | 22.5 | DegreesCelsius | R/W
7 | Economiser Outside Max Temperature | HoldingRegister | 428 | Real | AnalogValue | A705 | 732 | 0 | 26 | DegreesCelsius | R/W
7 | Economiser Minimum Damper | HoldingRegister | 430 | Real | AnalogValue | A706 | 733 | 0 | 10 | Volts | R/W
7 | Economiser Maximum Damper | HoldingRegister | 432 | Real | AnalogValue | A707 | 734 | 0 | 10 | Volts | R/W
7 | Economiser Outside Max Moisture | HoldingRegister | 434 | Real | AnalogValue | A708 | 735 | 0 | 100 | GramsPerKilogram | R/W
7 | Economiser Outside Max Dew Point | HoldingRegister | 436 | Real | AnalogValue | A709 | 736 | 0 | 100 | DegreesCelsius | R/W
7 | Economiser Outside Max Enthalpy | HoldingRegister | 438 | Real | AnalogValue | A710 | 737 | 0 | 100 | KilojoulesPerKilogram | R/W
7 | Economiser Enthalpy Delta | HoldingRegister | 440 | Real | AnalogValue | A711 | 738 | 0 | 10 | KilojoulesPerKilogram | R/W
7 | Economiser CO₂ Minimum Damper | HoldingRegister | 442 | Real | AnalogValue | A712 | 739 | 0 | 10 | Volts | R/W
7 | Economiser CO₂ Maximum Damper | HoldingRegister | 444 | Real | AnalogValue | A713 | 740 | 0 | 10 | Volts | R/W
7 | Room Temperature | InputRegister | 422 | Real | AnalogValue | A715 | 1121 | -99.9 | 99.9 | DegreesCelsius | R
7 | Indoor Room Temperature | InputRegister | 424 | Real | AnalogValue | A716 | 1122 | -99.9 | 99.9 | DegreesCelsius | R
7 | Outside Temperature | InputRegister | 426 | Real | AnalogValue | A717 | 1123 | -99.9 | 99.9 | DegreesCelsius | R
7 | Outside Air Temperature | InputRegister | 428 | Real | AnalogValue | A718 | 1124 | -99.9 | 99.9 | DegreesCelsius | R
7 | Compressor 1 Suction Temperature | InputRegister | 430 | Real | AnalogValue | A719 | 1125 | -999.9 | 999.9 | DegreesCelsius | R
7 | Compressor 1 Discharge Temperature | InputRegister | 432 | Real | AnalogValue | A720 | 1126 | -999.9 | 999.9 | DegreesCelsius | R
7 | Compressor 1 Suction SuperHeat | InputRegister | 434 | Real | AnalogValue | A721 | 1127 | -99.9 | 99.9 | DegreesCelsius | R
7 | Compressor 1 Suction SuperHeat Target | InputRegister | 436 | Real | AnalogValue | A722 | 1128 | -99.9 | 99.9 | DegreesCelsius | R
7 | Outdoor Coil 1 Temperature | InputRegister | 438 | Real | AnalogValue | A723 | 1129 | -99.9 | 99.9 | DegreesCelsius | R
7 | Indoor Coil 1 Temperature | InputRegister | 440 | Real | AnalogValue | A724 | 1130 | -99.9 | 99.9 | DegreesCelsius | R
7 | Wall Control 1 Temperature | InputRegister | 442 | Real | AnalogValue | A725 | 1131 | -99.9 | 99.9 | DegreesCelsius | R
7 | Wall Control 2 Temperature | InputRegister | 444 | Real | AnalogValue | A726 | 1132 | -99.9 | 99.9 | DegreesCelsius | R
7 | Wall Control 3 Temperature | InputRegister | 446 | Real | AnalogValue | A727 | 1133 | -99.9 | 99.9 | DegreesCelsius | R
7 | Auxillary Sensor 1 Temperature | InputRegister | 448 | Real | AnalogValue | A728 | 1134 | -99.9 | 99.9 | DegreesCelsius | R
7 | Auxillary Sensor 2 Temperature | InputRegister | 450 | Real | AnalogValue | A729 | 1135 | -99.9 | 99.9 | DegreesCelsius | R
7 | Auxillary Sensor 3 Temperature | InputRegister | 452 | Real | AnalogValue | A730 | 1136 | -99.9 | 99.9 | DegreesCelsius | R
7 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 446 | Real | AnalogValue | A731 | 741 | 0 | 100 | Percent | R/W
7 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 448 | Real | AnalogValue | A732 | 742 | 0 | 100 | Percent | R/W
7 | Reduced Airflow Speed | HoldingRegister | 450 | Real | AnalogValue | A733 | 743 | 0 | 100 | Percent | R/W
7 | Economiser Outside Max Humidity | HoldingRegister | 452 | Real | AnalogValue | A734 | 744 | 0 | 100 | Percent | R/W
7 | Actual System Running Capacity | InputRegister | 454 | Real | AnalogValue | A735 | 1137 | 0 | 100 | Percent | R
7 | Compressor 1 Demand | InputRegister | 456 | Real | AnalogValue | A736 | 1138 | 0 | 100 | Percent | R
7 | Compressor 1 Speed | InputRegister | 458 | Real | AnalogValue | A737 | 1139 | 0 | 100 | Percent | R
7 | Indoor Coil 1 Fan Speed | InputRegister | 460 | Real | AnalogValue | A738 | 1140 | 0 | 100 | Percent | R
7 | Compressor 1 EEV position | InputRegister | 462 | Real | AnalogValue | A739 | 1141 | 0 | 100 | Percent | R
7 | Generic Analog 01 | HoldingRegister | 454 | Real | AnalogValue | A740 | 745 |  |  |  | R/W
7 | Generic Analog 02 | HoldingRegister | 456 | Real | AnalogValue | A741 | 746 |  |  |  | R/W
7 | Generic Analog 03 | HoldingRegister | 458 | Real | AnalogValue | A742 | 747 |  |  |  | R/W
7 | Generic Analog 04 | HoldingRegister | 460 | Real | AnalogValue | A743 | 748 |  |  |  | R/W
7 | Generic Analog 05 | HoldingRegister | 462 | Real | AnalogValue | A744 | 749 |  |  |  | R/W
7 | Turns the AC Off/On (0=Off, 1=On) | Coil | 180 | Bool | BinaryValue | D701 | 163 |  |  |  | R/W
7 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 181 | Bool | BinaryValue | D702 | 164 |  |  |  | R/W
7 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 182 | Bool | BinaryValue | D703 | 165 |  |  |  | R/W
7 | Set Turbo Mode (0=Off, 1=On) | Coil | 183 | Bool | BinaryValue | D704 | 166 |  |  |  | R/W
7 | Set Quiet Mode (0=Off, 1=On) | Coil | 184 | Bool | BinaryValue | D705 | 167 |  |  |  | R/W
7 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 185 | Bool | BinaryValue | D706 | 168 |  |  |  | R/W
7 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 188 | Bool | BinaryValue | D709 | 171 |  |  |  | R/W
7 | Enable Economiser (0=Off, 1=On) | Coil | 189 | Bool | BinaryValue | D710 | 172 |  |  |  | R/W
7 | Enable Humidity Control | Coil | 190 | Bool | BinaryValue | D711 | 173 |  |  |  | R/W
7 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 191 | Bool | BinaryValue | D712 | 174 |  |  |  | R/W
7 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 192 | Bool | BinaryValue | D713 | 175 |  |  |  | R/W
7 | Enable CO₂ Control (0=Off, 1=On) | Coil | 193 | Bool | BinaryValue | D714 | 176 |  |  |  | R/W
7 | Alarm Output (0=Off, 1=On) | DiscreteInput | 180 | Bool | BinaryValue | D715 | 414 |  |  |  | R
7 | Air Filter Notification | DiscreteInput | 181 | Bool | BinaryValue | D716 | 415 |  |  |  | R
7 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 184 | Bool | BinaryValue | D719 | 418 |  |  |  | R
7 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 185 | Bool | BinaryValue | D720 | 419 |  |  |  | R
7 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 186 | Bool | BinaryValue | D721 | 420 |  |  |  | R
7 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 187 | Bool | BinaryValue | D722 | 421 |  |  |  | R
7 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 188 | Bool | BinaryValue | D723 | 422 |  |  |  | R
7 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 189 | Bool | BinaryValue | D724 | 423 |  |  |  | R
7 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 190 | Bool | BinaryValue | D725 | 424 |  |  |  | R
7 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 191 | Bool | BinaryValue | D726 | 425 |  |  |  | R
7 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 192 | Bool | BinaryValue | D727 | 426 |  |  |  | R
7 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 193 | Bool | BinaryValue | D728 | 427 |  |  |  | R
7 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 194 | Bool | BinaryValue | D729 | 428 |  |  |  | R
7 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 195 | Bool | BinaryValue | D730 | 429 |  |  |  | R
7 | Compressor 1 Discharge Temp High | DiscreteInput | 196 | Bool | BinaryValue | D731 | 430 |  |  |  | R
7 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 197 | Bool | BinaryValue | D732 | 431 |  |  |  | R
7 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 198 | Bool | BinaryValue | D733 | 432 |  |  |  | R
7 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 199 | Bool | BinaryValue | D734 | 433 |  |  |  | R
7 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 200 | Bool | BinaryValue | D735 | 434 |  |  |  | R
7 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 201 | Bool | BinaryValue | D736 | 435 |  |  |  | R
7 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 202 | Bool | BinaryValue | D737 | 436 |  |  |  | R
7 | Set zone 1 (0=Off, 1=On) | Coil | 194 | Bool | BinaryValue | D738 | 177 |  |  |  | R/W
7 | Set zone 2 (0=Off, 1=On) | Coil | 195 | Bool | BinaryValue | D739 | 178 |  |  |  | R/W
7 | Set zone 3 (0=Off, 1=On) | Coil | 196 | Bool | BinaryValue | D740 | 179 |  |  |  | R/W
7 | Set zone 4 (0=Off, 1=On) | Coil | 197 | Bool | BinaryValue | D741 | 180 |  |  |  | R/W
7 | Set zone 5 (0=Off, 1=On) | Coil | 198 | Bool | BinaryValue | D742 | 181 |  |  |  | R/W
7 | Set zone 6 (0=Off, 1=On) | Coil | 199 | Bool | BinaryValue | D743 | 182 |  |  |  | R/W
7 | Set zone 7 (0=Off, 1=On) | Coil | 200 | Bool | BinaryValue | D744 | 183 |  |  |  | R/W
7 | Set zone 8 (0=Off, 1=On) | Coil | 201 | Bool | BinaryValue | D745 | 184 |  |  |  | R/W
7 | Generic Digital 1 | Coil | 202 | Bool | BinaryValue | D746 | 185 |  |  |  | R/W
7 | Generic Digital 2 | Coil | 203 | Bool | BinaryValue | D747 | 186 |  |  |  | R/W
7 | Generic Digital 3 | Coil | 204 | Bool | BinaryValue | D748 | 187 |  |  |  | R/W
7 | Generic Digital 4 | Coil | 205 | Bool | BinaryValue | D749 | 188 |  |  |  | R/W
7 | Generic Digital 5 | Coil | 206 | Bool | BinaryValue | D750 | 189 |  |  |  | R/W
7 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 464 | Int | IntegerValue | I701 | 750 | 1 | 4 |  | R/W
7 | Set Air Filter Notification Timer | HoldingRegister | 465 | Int | IntegerValue | I702 | 751 | 1 | 10000 | Hours | R/W
7 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 466 | Int | IntegerValue | I703 | 752 | 1 | 4 |  | R/W
7 | Target Airflow | HoldingRegister | 467 | Int | IntegerValue | I704 | 753 | 0 | 6000 | LitersPerSecond | R/W
7 | Enable Volumetric Airflow | HoldingRegister | 468 | Int | IntegerValue | I705 | 754 | 0 | 6000 | LitersPerSecond | R/W
7 | Indoor Pressure Filter level warning | HoldingRegister | 469 | Int | IntegerValue | I706 | 755 | 0 | 6000 | Pascals | R/W
7 | Economiser CO₂ Low Level | HoldingRegister | 470 | Int | IntegerValue | I707 | 756 | 0 | 1000 | PartsPerMillion | R/W
7 | Economiser CO₂ High Level | HoldingRegister | 471 | Int | IntegerValue | I708 | 757 | 0 | 1000 | PartsPerMillion | R/W
7 | BMS card Software version | InputRegister | 464 | Int | IntegerValue | I709 | 1142 | 0 | 32767 |  | R
7 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 465 | Int | IntegerValue | I710 | 1143 | 0 | 2 |  | R
7 | Air Filter Run Timer | InputRegister | 466 | Int | IntegerValue | I711 | 1144 | 0 | 10000 | Hours | R
7 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 467 | Int | IntegerValue | I712 | 1145 | 0 | 4 |  | R
7 | Indoor Airflow | InputRegister | 468 | Int | IntegerValue | I713 | 1146 | 0 | 6000 | LitersPerSecond | R
7 | Indoor Static Pressure | InputRegister | 469 | Int | IntegerValue | I714 | 1147 | 0 | 6000 | Pascals | R
7 | Measured CO₂ level | InputRegister | 470 | Int | IntegerValue | I715 | 1148 | 0 | 1000 | PartsPerMillion | R
7 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 471 | Int | IntegerValue | I716 | 1149 | 0 | 100 |  | R
7 | Error History Log, 1 error ago | InputRegister | 472 | Int | IntegerValue | I717 | 1150 | 0 | 100 |  | R
7 | Error History Log, 2 errors ago | InputRegister | 473 | Int | IntegerValue | I718 | 1151 | 0 | 100 |  | R
7 | Error History Log, 3 errors ago | InputRegister | 474 | Int | IntegerValue | I719 | 1152 | 0 | 100 |  | R
7 | Error History Log, 4 errors ago | InputRegister | 475 | Int | IntegerValue | I720 | 1153 | 0 | 100 |  | R
7 | Error History Log, 5 errors ago | InputRegister | 476 | Int | IntegerValue | I721 | 1154 | 0 | 100 |  | R
7 | Outdoor Unit 1 Model | InputRegister | 477 | Int | IntegerValue | I722 | 1155 | 0 | 32767 |  | R
7 | Outdoor Unit 1 Software version | InputRegister | 478 | Int | IntegerValue | I723 | 1156 | 0 | 32767 |  | R
7 | Compressor 1 Type | InputRegister | 479 | Int | IntegerValue | I724 | 1157 | 0 | 100 |  | R
7 | Compressor 1 Suction Pressure | InputRegister | 480 | Int | IntegerValue | I725 | 1158 | 0 | 6000 | KiloPascals | R
7 | Compressor 1 Discharge Pressure | InputRegister | 481 | Int | IntegerValue | I726 | 1159 | 0 | 6000 | KiloPascals | R
7 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 482 | Int | IntegerValue | I727 | 1160 | 0 | 3 |  | R
7 | Indoor Coil 1 Fan 1 Speed | InputRegister | 483 | Int | IntegerValue | I728 | 1161 | 0 | 9999 | RevolutionsPerMinute | R
7 | Generic Integer 1 | HoldingRegister | 472 | Int | IntegerValue | I729 | 758 |  |  |  | R/W
7 | Generic Integer 2 | HoldingRegister | 473 | Int | IntegerValue | I730 | 759 |  |  |  | R/W
7 | Generic Integer 3 | HoldingRegister | 474 | Int | IntegerValue | I731 | 760 |  |  |  | R/W
7 | Generic Integer 4 | HoldingRegister | 475 | Int | IntegerValue | I732 | 761 |  |  |  | R/W
7 | Generic Integer 5 | HoldingRegister | 476 | Int | IntegerValue | I733 | 762 |  |  |  | R/W

## Device 8
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
8 | Set Master Setpoint Temperature | HoldingRegister | 490 | Real | AnalogValue | A801 | 763 | 16 | 30 | DegreesCelsius | R/W
8 | Economiser Temperature Difference | HoldingRegister | 494 | Real | AnalogValue | A803 | 765 | 0 | 10 | DegreesCelsius | R/W
8 | Economiser Outside Min Temperature | HoldingRegister | 496 | Real | AnalogValue | A804 | 766 | 0 | 22.5 | DegreesCelsius | R/W
8 | Economiser Outside Max Temperature | HoldingRegister | 498 | Real | AnalogValue | A805 | 767 | 0 | 26 | DegreesCelsius | R/W
8 | Economiser Minimum Damper | HoldingRegister | 500 | Real | AnalogValue | A806 | 768 | 0 | 10 | Volts | R/W
8 | Economiser Maximum Damper | HoldingRegister | 502 | Real | AnalogValue | A807 | 769 | 0 | 10 | Volts | R/W
8 | Economiser Outside Max Moisture | HoldingRegister | 504 | Real | AnalogValue | A808 | 770 | 0 | 100 | GramsPerKilogram | R/W
8 | Economiser Outside Max Dew Point | HoldingRegister | 506 | Real | AnalogValue | A809 | 771 | 0 | 100 | DegreesCelsius | R/W
8 | Economiser Outside Max Enthalpy | HoldingRegister | 508 | Real | AnalogValue | A810 | 772 | 0 | 100 | KilojoulesPerKilogram | R/W
8 | Economiser Enthalpy Delta | HoldingRegister | 510 | Real | AnalogValue | A811 | 773 | 0 | 10 | KilojoulesPerKilogram | R/W
8 | Economiser CO₂ Minimum Damper | HoldingRegister | 512 | Real | AnalogValue | A812 | 774 | 0 | 10 | Volts | R/W
8 | Economiser CO₂ Maximum Damper | HoldingRegister | 514 | Real | AnalogValue | A813 | 775 | 0 | 10 | Volts | R/W
8 | Room Temperature | InputRegister | 492 | Real | AnalogValue | A815 | 1163 | -99.9 | 99.9 | DegreesCelsius | R
8 | Indoor Room Temperature | InputRegister | 494 | Real | AnalogValue | A816 | 1164 | -99.9 | 99.9 | DegreesCelsius | R
8 | Outside Temperature | InputRegister | 496 | Real | AnalogValue | A817 | 1165 | -99.9 | 99.9 | DegreesCelsius | R
8 | Outside Air Temperature | InputRegister | 498 | Real | AnalogValue | A818 | 1166 | -99.9 | 99.9 | DegreesCelsius | R
8 | Compressor 1 Suction Temperature | InputRegister | 500 | Real | AnalogValue | A819 | 1167 | -999.9 | 999.9 | DegreesCelsius | R
8 | Compressor 1 Discharge Temperature | InputRegister | 502 | Real | AnalogValue | A820 | 1168 | -999.9 | 999.9 | DegreesCelsius | R
8 | Compressor 1 Suction SuperHeat | InputRegister | 504 | Real | AnalogValue | A821 | 1169 | -99.9 | 99.9 | DegreesCelsius | R
8 | Compressor 1 Suction SuperHeat Target | InputRegister | 506 | Real | AnalogValue | A822 | 1170 | -99.9 | 99.9 | DegreesCelsius | R
8 | Outdoor Coil 1 Temperature | InputRegister | 508 | Real | AnalogValue | A823 | 1171 | -99.9 | 99.9 | DegreesCelsius | R
8 | Indoor Coil 1 Temperature | InputRegister | 510 | Real | AnalogValue | A824 | 1172 | -99.9 | 99.9 | DegreesCelsius | R
8 | Wall Control 1 Temperature | InputRegister | 512 | Real | AnalogValue | A825 | 1173 | -99.9 | 99.9 | DegreesCelsius | R
8 | Wall Control 2 Temperature | InputRegister | 514 | Real | AnalogValue | A826 | 1174 | -99.9 | 99.9 | DegreesCelsius | R
8 | Wall Control 3 Temperature | InputRegister | 516 | Real | AnalogValue | A827 | 1175 | -99.9 | 99.9 | DegreesCelsius | R
8 | Auxillary Sensor 1 Temperature | InputRegister | 518 | Real | AnalogValue | A828 | 1176 | -99.9 | 99.9 | DegreesCelsius | R
8 | Auxillary Sensor 2 Temperature | InputRegister | 520 | Real | AnalogValue | A829 | 1177 | -99.9 | 99.9 | DegreesCelsius | R
8 | Auxillary Sensor 3 Temperature | InputRegister | 522 | Real | AnalogValue | A830 | 1178 | -99.9 | 99.9 | DegreesCelsius | R
8 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 516 | Real | AnalogValue | A831 | 776 | 0 | 100 | Percent | R/W
8 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 518 | Real | AnalogValue | A832 | 777 | 0 | 100 | Percent | R/W
8 | Reduced Airflow Speed | HoldingRegister | 520 | Real | AnalogValue | A833 | 778 | 0 | 100 | Percent | R/W
8 | Economiser Outside Max Humidity | HoldingRegister | 522 | Real | AnalogValue | A834 | 779 | 0 | 100 | Percent | R/W
8 | Actual System Running Capacity | InputRegister | 524 | Real | AnalogValue | A835 | 1179 | 0 | 100 | Percent | R
8 | Compressor 1 Demand | InputRegister | 526 | Real | AnalogValue | A836 | 1180 | 0 | 100 | Percent | R
8 | Compressor 1 Speed | InputRegister | 528 | Real | AnalogValue | A837 | 1181 | 0 | 100 | Percent | R
8 | Indoor Coil 1 Fan Speed | InputRegister | 530 | Real | AnalogValue | A838 | 1182 | 0 | 100 | Percent | R
8 | Compressor 1 EEV position | InputRegister | 532 | Real | AnalogValue | A839 | 1183 | 0 | 100 | Percent | R
8 | Generic Analog 01 | HoldingRegister | 524 | Real | AnalogValue | A840 | 780 |  |  |  | R/W
8 | Generic Analog 02 | HoldingRegister | 526 | Real | AnalogValue | A841 | 781 |  |  |  | R/W
8 | Generic Analog 03 | HoldingRegister | 528 | Real | AnalogValue | A842 | 782 |  |  |  | R/W
8 | Generic Analog 04 | HoldingRegister | 530 | Real | AnalogValue | A843 | 783 |  |  |  | R/W
8 | Generic Analog 05 | HoldingRegister | 532 | Real | AnalogValue | A844 | 784 |  |  |  | R/W
8 | Turns the AC Off/On (0=Off, 1=On) | Coil | 210 | Bool | BinaryValue | D801 | 190 |  |  |  | R/W
8 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 211 | Bool | BinaryValue | D802 | 191 |  |  |  | R/W
8 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 212 | Bool | BinaryValue | D803 | 192 |  |  |  | R/W
8 | Set Turbo Mode (0=Off, 1=On) | Coil | 213 | Bool | BinaryValue | D804 | 193 |  |  |  | R/W
8 | Set Quiet Mode (0=Off, 1=On) | Coil | 214 | Bool | BinaryValue | D805 | 194 |  |  |  | R/W
8 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 215 | Bool | BinaryValue | D806 | 195 |  |  |  | R/W
8 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 218 | Bool | BinaryValue | D809 | 198 |  |  |  | R/W
8 | Enable Economiser (0=Off, 1=On) | Coil | 219 | Bool | BinaryValue | D810 | 199 |  |  |  | R/W
8 | Enable Humidity Control | Coil | 220 | Bool | BinaryValue | D811 | 200 |  |  |  | R/W
8 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 221 | Bool | BinaryValue | D812 | 201 |  |  |  | R/W
8 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 222 | Bool | BinaryValue | D813 | 202 |  |  |  | R/W
8 | Enable CO₂ Control (0=Off, 1=On) | Coil | 223 | Bool | BinaryValue | D814 | 203 |  |  |  | R/W
8 | Alarm Output (0=Off, 1=On) | DiscreteInput | 210 | Bool | BinaryValue | D815 | 437 |  |  |  | R
8 | Air Filter Notification | DiscreteInput | 211 | Bool | BinaryValue | D816 | 438 |  |  |  | R
8 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 214 | Bool | BinaryValue | D819 | 441 |  |  |  | R
8 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 215 | Bool | BinaryValue | D820 | 442 |  |  |  | R
8 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 216 | Bool | BinaryValue | D821 | 443 |  |  |  | R
8 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 217 | Bool | BinaryValue | D822 | 444 |  |  |  | R
8 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 218 | Bool | BinaryValue | D823 | 445 |  |  |  | R
8 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 219 | Bool | BinaryValue | D824 | 446 |  |  |  | R
8 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 220 | Bool | BinaryValue | D825 | 447 |  |  |  | R
8 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 221 | Bool | BinaryValue | D826 | 448 |  |  |  | R
8 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 222 | Bool | BinaryValue | D827 | 449 |  |  |  | R
8 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 223 | Bool | BinaryValue | D828 | 450 |  |  |  | R
8 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 224 | Bool | BinaryValue | D829 | 451 |  |  |  | R
8 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 225 | Bool | BinaryValue | D830 | 452 |  |  |  | R
8 | Compressor 1 Discharge Temp High | DiscreteInput | 226 | Bool | BinaryValue | D831 | 453 |  |  |  | R
8 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 227 | Bool | BinaryValue | D832 | 454 |  |  |  | R
8 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 228 | Bool | BinaryValue | D833 | 455 |  |  |  | R
8 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 229 | Bool | BinaryValue | D834 | 456 |  |  |  | R
8 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 230 | Bool | BinaryValue | D835 | 457 |  |  |  | R
8 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 231 | Bool | BinaryValue | D836 | 458 |  |  |  | R
8 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 232 | Bool | BinaryValue | D837 | 459 |  |  |  | R
8 | Set zone 1 (0=Off, 1=On) | Coil | 224 | Bool | BinaryValue | D838 | 204 |  |  |  | R/W
8 | Set zone 2 (0=Off, 1=On) | Coil | 225 | Bool | BinaryValue | D839 | 205 |  |  |  | R/W
8 | Set zone 3 (0=Off, 1=On) | Coil | 226 | Bool | BinaryValue | D840 | 206 |  |  |  | R/W
8 | Set zone 4 (0=Off, 1=On) | Coil | 227 | Bool | BinaryValue | D841 | 207 |  |  |  | R/W
8 | Set zone 5 (0=Off, 1=On) | Coil | 228 | Bool | BinaryValue | D842 | 208 |  |  |  | R/W
8 | Set zone 6 (0=Off, 1=On) | Coil | 229 | Bool | BinaryValue | D843 | 209 |  |  |  | R/W
8 | Set zone 7 (0=Off, 1=On) | Coil | 230 | Bool | BinaryValue | D844 | 210 |  |  |  | R/W
8 | Set zone 8 (0=Off, 1=On) | Coil | 231 | Bool | BinaryValue | D845 | 211 |  |  |  | R/W
8 | Generic Digital 1 | Coil | 232 | Bool | BinaryValue | D846 | 212 |  |  |  | R/W
8 | Generic Digital 2 | Coil | 233 | Bool | BinaryValue | D847 | 213 |  |  |  | R/W
8 | Generic Digital 3 | Coil | 234 | Bool | BinaryValue | D848 | 214 |  |  |  | R/W
8 | Generic Digital 4 | Coil | 235 | Bool | BinaryValue | D849 | 215 |  |  |  | R/W
8 | Generic Digital 5 | Coil | 236 | Bool | BinaryValue | D850 | 216 |  |  |  | R/W
8 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 534 | Int | IntegerValue | I801 | 785 | 1 | 4 |  | R/W
8 | Set Air Filter Notification Timer | HoldingRegister | 535 | Int | IntegerValue | I802 | 786 | 1 | 10000 | Hours | R/W
8 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 536 | Int | IntegerValue | I803 | 787 | 1 | 4 |  | R/W
8 | Target Airflow | HoldingRegister | 537 | Int | IntegerValue | I804 | 788 | 0 | 6000 | LitersPerSecond | R/W
8 | Enable Volumetric Airflow | HoldingRegister | 538 | Int | IntegerValue | I805 | 789 | 0 | 6000 | LitersPerSecond | R/W
8 | Indoor Pressure Filter level warning | HoldingRegister | 539 | Int | IntegerValue | I806 | 790 | 0 | 6000 | Pascals | R/W
8 | Economiser CO₂ Low Level | HoldingRegister | 540 | Int | IntegerValue | I807 | 791 | 0 | 1000 | PartsPerMillion | R/W
8 | Economiser CO₂ High Level | HoldingRegister | 541 | Int | IntegerValue | I808 | 792 | 0 | 1000 | PartsPerMillion | R/W
8 | BMS card Software version | InputRegister | 534 | Int | IntegerValue | I809 | 1184 | 0 | 32767 |  | R
8 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 535 | Int | IntegerValue | I810 | 1185 | 0 | 2 |  | R
8 | Air Filter Run Timer | InputRegister | 536 | Int | IntegerValue | I811 | 1186 | 0 | 10000 | Hours | R
8 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 537 | Int | IntegerValue | I812 | 1187 | 0 | 4 |  | R
8 | Indoor Airflow | InputRegister | 538 | Int | IntegerValue | I813 | 1188 | 0 | 6000 | LitersPerSecond | R
8 | Indoor Static Pressure | InputRegister | 539 | Int | IntegerValue | I814 | 1189 | 0 | 6000 | Pascals | R
8 | Measured CO₂ level | InputRegister | 540 | Int | IntegerValue | I815 | 1190 | 0 | 1000 | PartsPerMillion | R
8 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 541 | Int | IntegerValue | I816 | 1191 | 0 | 100 |  | R
8 | Error History Log, 1 error ago | InputRegister | 542 | Int | IntegerValue | I817 | 1192 | 0 | 100 |  | R
8 | Error History Log, 2 errors ago | InputRegister | 543 | Int | IntegerValue | I818 | 1193 | 0 | 100 |  | R
8 | Error History Log, 3 errors ago | InputRegister | 544 | Int | IntegerValue | I819 | 1194 | 0 | 100 |  | R
8 | Error History Log, 4 errors ago | InputRegister | 545 | Int | IntegerValue | I820 | 1195 | 0 | 100 |  | R
8 | Error History Log, 5 errors ago | InputRegister | 546 | Int | IntegerValue | I821 | 1196 | 0 | 100 |  | R
8 | Outdoor Unit 1 Model | InputRegister | 547 | Int | IntegerValue | I822 | 1197 | 0 | 32767 |  | R
8 | Outdoor Unit 1 Software version | InputRegister | 548 | Int | IntegerValue | I823 | 1198 | 0 | 32767 |  | R
8 | Compressor 1 Type | InputRegister | 549 | Int | IntegerValue | I824 | 1199 | 0 | 100 |  | R
8 | Compressor 1 Suction Pressure | InputRegister | 550 | Int | IntegerValue | I825 | 1200 | 0 | 6000 | KiloPascals | R
8 | Compressor 1 Discharge Pressure | InputRegister | 551 | Int | IntegerValue | I826 | 1201 | 0 | 6000 | KiloPascals | R
8 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 552 | Int | IntegerValue | I827 | 1202 | 0 | 3 |  | R
8 | Indoor Coil 1 Fan 1 Speed | InputRegister | 553 | Int | IntegerValue | I828 | 1203 | 0 | 9999 | RevolutionsPerMinute | R
8 | Generic Integer 1 | HoldingRegister | 542 | Int | IntegerValue | I829 | 793 |  |  |  | R/W
8 | Generic Integer 2 | HoldingRegister | 543 | Int | IntegerValue | I830 | 794 |  |  |  | R/W
8 | Generic Integer 3 | HoldingRegister | 544 | Int | IntegerValue | I831 | 795 |  |  |  | R/W
8 | Generic Integer 4 | HoldingRegister | 545 | Int | IntegerValue | I832 | 796 |  |  |  | R/W
8 | Generic Integer 5 | HoldingRegister | 546 | Int | IntegerValue | I833 | 797 |  |  |  | R/W

## Device 9
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
9 | Set Master Setpoint Temperature | HoldingRegister | 560 | Real | AnalogValue | A901 | 798 | 16 | 30 | DegreesCelsius | R/W
9 | Economiser Temperature Difference | HoldingRegister | 564 | Real | AnalogValue | A903 | 800 | 0 | 10 | DegreesCelsius | R/W
9 | Economiser Outside Min Temperature | HoldingRegister | 566 | Real | AnalogValue | A904 | 801 | 0 | 22.5 | DegreesCelsius | R/W
9 | Economiser Outside Max Temperature | HoldingRegister | 568 | Real | AnalogValue | A905 | 802 | 0 | 26 | DegreesCelsius | R/W
9 | Economiser Minimum Damper | HoldingRegister | 570 | Real | AnalogValue | A906 | 803 | 0 | 10 | Volts | R/W
9 | Economiser Maximum Damper | HoldingRegister | 572 | Real | AnalogValue | A907 | 804 | 0 | 10 | Volts | R/W
9 | Economiser Outside Max Moisture | HoldingRegister | 574 | Real | AnalogValue | A908 | 805 | 0 | 100 | GramsPerKilogram | R/W
9 | Economiser Outside Max Dew Point | HoldingRegister | 576 | Real | AnalogValue | A909 | 806 | 0 | 100 | DegreesCelsius | R/W
9 | Economiser Outside Max Enthalpy | HoldingRegister | 578 | Real | AnalogValue | A910 | 807 | 0 | 100 | KilojoulesPerKilogram | R/W
9 | Economiser Enthalpy Delta | HoldingRegister | 580 | Real | AnalogValue | A911 | 808 | 0 | 10 | KilojoulesPerKilogram | R/W
9 | Economiser CO₂ Minimum Damper | HoldingRegister | 582 | Real | AnalogValue | A912 | 809 | 0 | 10 | Volts | R/W
9 | Economiser CO₂ Maximum Damper | HoldingRegister | 584 | Real | AnalogValue | A913 | 810 | 0 | 10 | Volts | R/W
9 | Room Temperature | InputRegister | 562 | Real | AnalogValue | A915 | 1205 | -99.9 | 99.9 | DegreesCelsius | R
9 | Indoor Room Temperature | InputRegister | 564 | Real | AnalogValue | A916 | 1206 | -99.9 | 99.9 | DegreesCelsius | R
9 | Outside Temperature | InputRegister | 566 | Real | AnalogValue | A917 | 1207 | -99.9 | 99.9 | DegreesCelsius | R
9 | Outside Air Temperature | InputRegister | 568 | Real | AnalogValue | A918 | 1208 | -99.9 | 99.9 | DegreesCelsius | R
9 | Compressor 1 Suction Temperature | InputRegister | 570 | Real | AnalogValue | A919 | 1209 | -999.9 | 999.9 | DegreesCelsius | R
9 | Compressor 1 Discharge Temperature | InputRegister | 572 | Real | AnalogValue | A920 | 1210 | -999.9 | 999.9 | DegreesCelsius | R
9 | Compressor 1 Suction SuperHeat | InputRegister | 574 | Real | AnalogValue | A921 | 1211 | -99.9 | 99.9 | DegreesCelsius | R
9 | Compressor 1 Suction SuperHeat Target | InputRegister | 576 | Real | AnalogValue | A922 | 1212 | -99.9 | 99.9 | DegreesCelsius | R
9 | Outdoor Coil 1 Temperature | InputRegister | 578 | Real | AnalogValue | A923 | 1213 | -99.9 | 99.9 | DegreesCelsius | R
9 | Indoor Coil 1 Temperature | InputRegister | 580 | Real | AnalogValue | A924 | 1214 | -99.9 | 99.9 | DegreesCelsius | R
9 | Wall Control 1 Temperature | InputRegister | 582 | Real | AnalogValue | A925 | 1215 | -99.9 | 99.9 | DegreesCelsius | R
9 | Wall Control 2 Temperature | InputRegister | 584 | Real | AnalogValue | A926 | 1216 | -99.9 | 99.9 | DegreesCelsius | R
9 | Wall Control 3 Temperature | InputRegister | 586 | Real | AnalogValue | A927 | 1217 | -99.9 | 99.9 | DegreesCelsius | R
9 | Auxillary Sensor 1 Temperature | InputRegister | 588 | Real | AnalogValue | A928 | 1218 | -99.9 | 99.9 | DegreesCelsius | R
9 | Auxillary Sensor 2 Temperature | InputRegister | 590 | Real | AnalogValue | A929 | 1219 | -99.9 | 99.9 | DegreesCelsius | R
9 | Auxillary Sensor 3 Temperature | InputRegister | 592 | Real | AnalogValue | A930 | 1220 | -99.9 | 99.9 | DegreesCelsius | R
9 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 586 | Real | AnalogValue | A931 | 811 | 0 | 100 | Percent | R/W
9 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 588 | Real | AnalogValue | A932 | 812 | 0 | 100 | Percent | R/W
9 | Reduced Airflow Speed | HoldingRegister | 590 | Real | AnalogValue | A933 | 813 | 0 | 100 | Percent | R/W
9 | Economiser Outside Max Humidity | HoldingRegister | 592 | Real | AnalogValue | A934 | 814 | 0 | 100 | Percent | R/W
9 | Actual System Running Capacity | InputRegister | 594 | Real | AnalogValue | A935 | 1221 | 0 | 100 | Percent | R
9 | Compressor 1 Demand | InputRegister | 596 | Real | AnalogValue | A936 | 1222 | 0 | 100 | Percent | R
9 | Compressor 1 Speed | InputRegister | 598 | Real | AnalogValue | A937 | 1223 | 0 | 100 | Percent | R
9 | Indoor Coil 1 Fan Speed | InputRegister | 600 | Real | AnalogValue | A938 | 1224 | 0 | 100 | Percent | R
9 | Compressor 1 EEV position | InputRegister | 602 | Real | AnalogValue | A939 | 1225 | 0 | 100 | Percent | R
9 | Generic Analog 01 | HoldingRegister | 594 | Real | AnalogValue | A940 | 815 |  |  |  | R/W
9 | Generic Analog 02 | HoldingRegister | 596 | Real | AnalogValue | A941 | 816 |  |  |  | R/W
9 | Generic Analog 03 | HoldingRegister | 598 | Real | AnalogValue | A942 | 817 |  |  |  | R/W
9 | Generic Analog 04 | HoldingRegister | 600 | Real | AnalogValue | A943 | 818 |  |  |  | R/W
9 | Generic Analog 05 | HoldingRegister | 602 | Real | AnalogValue | A944 | 819 |  |  |  | R/W
9 | Turns the AC Off/On (0=Off, 1=On) | Coil | 240 | Bool | BinaryValue | D901 | 217 |  |  |  | R/W
9 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 241 | Bool | BinaryValue | D902 | 218 |  |  |  | R/W
9 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 242 | Bool | BinaryValue | D903 | 219 |  |  |  | R/W
9 | Set Turbo Mode (0=Off, 1=On) | Coil | 243 | Bool | BinaryValue | D904 | 220 |  |  |  | R/W
9 | Set Quiet Mode (0=Off, 1=On) | Coil | 244 | Bool | BinaryValue | D905 | 221 |  |  |  | R/W
9 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 245 | Bool | BinaryValue | D906 | 222 |  |  |  | R/W
9 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 248 | Bool | BinaryValue | D909 | 225 |  |  |  | R/W
9 | Enable Economiser (0=Off, 1=On) | Coil | 249 | Bool | BinaryValue | D910 | 226 |  |  |  | R/W
9 | Enable Humidity Control | Coil | 250 | Bool | BinaryValue | D911 | 227 |  |  |  | R/W
9 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 251 | Bool | BinaryValue | D912 | 228 |  |  |  | R/W
9 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 252 | Bool | BinaryValue | D913 | 229 |  |  |  | R/W
9 | Enable CO₂ Control (0=Off, 1=On) | Coil | 253 | Bool | BinaryValue | D914 | 230 |  |  |  | R/W
9 | Alarm Output (0=Off, 1=On) | DiscreteInput | 240 | Bool | BinaryValue | D915 | 460 |  |  |  | R
9 | Air Filter Notification | DiscreteInput | 241 | Bool | BinaryValue | D916 | 461 |  |  |  | R
9 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 244 | Bool | BinaryValue | D919 | 464 |  |  |  | R
9 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 245 | Bool | BinaryValue | D920 | 465 |  |  |  | R
9 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 246 | Bool | BinaryValue | D921 | 466 |  |  |  | R
9 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 247 | Bool | BinaryValue | D922 | 467 |  |  |  | R
9 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 248 | Bool | BinaryValue | D923 | 468 |  |  |  | R
9 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 249 | Bool | BinaryValue | D924 | 469 |  |  |  | R
9 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 250 | Bool | BinaryValue | D925 | 470 |  |  |  | R
9 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 251 | Bool | BinaryValue | D926 | 471 |  |  |  | R
9 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 252 | Bool | BinaryValue | D927 | 472 |  |  |  | R
9 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 253 | Bool | BinaryValue | D928 | 473 |  |  |  | R
9 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 254 | Bool | BinaryValue | D929 | 474 |  |  |  | R
9 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 255 | Bool | BinaryValue | D930 | 475 |  |  |  | R
9 | Compressor 1 Discharge Temp High | DiscreteInput | 256 | Bool | BinaryValue | D931 | 476 |  |  |  | R
9 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 257 | Bool | BinaryValue | D932 | 477 |  |  |  | R
9 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 258 | Bool | BinaryValue | D933 | 478 |  |  |  | R
9 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 259 | Bool | BinaryValue | D934 | 479 |  |  |  | R
9 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 260 | Bool | BinaryValue | D935 | 480 |  |  |  | R
9 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 261 | Bool | BinaryValue | D936 | 481 |  |  |  | R
9 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 262 | Bool | BinaryValue | D937 | 482 |  |  |  | R
9 | Set zone 1 (0=Off, 1=On) | Coil | 254 | Bool | BinaryValue | D938 | 231 |  |  |  | R/W
9 | Set zone 2 (0=Off, 1=On) | Coil | 255 | Bool | BinaryValue | D939 | 232 |  |  |  | R/W
9 | Set zone 3 (0=Off, 1=On) | Coil | 256 | Bool | BinaryValue | D940 | 233 |  |  |  | R/W
9 | Set zone 4 (0=Off, 1=On) | Coil | 257 | Bool | BinaryValue | D941 | 234 |  |  |  | R/W
9 | Set zone 5 (0=Off, 1=On) | Coil | 258 | Bool | BinaryValue | D942 | 235 |  |  |  | R/W
9 | Set zone 6 (0=Off, 1=On) | Coil | 259 | Bool | BinaryValue | D943 | 236 |  |  |  | R/W
9 | Set zone 7 (0=Off, 1=On) | Coil | 260 | Bool | BinaryValue | D944 | 237 |  |  |  | R/W
9 | Set zone 8 (0=Off, 1=On) | Coil | 261 | Bool | BinaryValue | D945 | 238 |  |  |  | R/W
9 | Generic Digital 1 | Coil | 262 | Bool | BinaryValue | D946 | 239 |  |  |  | R/W
9 | Generic Digital 2 | Coil | 263 | Bool | BinaryValue | D947 | 240 |  |  |  | R/W
9 | Generic Digital 3 | Coil | 264 | Bool | BinaryValue | D948 | 241 |  |  |  | R/W
9 | Generic Digital 4 | Coil | 265 | Bool | BinaryValue | D949 | 242 |  |  |  | R/W
9 | Generic Digital 5 | Coil | 266 | Bool | BinaryValue | D950 | 243 |  |  |  | R/W
9 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 604 | Int | IntegerValue | I901 | 820 | 1 | 4 |  | R/W
9 | Set Air Filter Notification Timer | HoldingRegister | 605 | Int | IntegerValue | I902 | 821 | 1 | 10000 | Hours | R/W
9 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 606 | Int | IntegerValue | I903 | 822 | 1 | 4 |  | R/W
9 | Target Airflow | HoldingRegister | 607 | Int | IntegerValue | I904 | 823 | 0 | 6000 | LitersPerSecond | R/W
9 | Enable Volumetric Airflow | HoldingRegister | 608 | Int | IntegerValue | I905 | 824 | 0 | 6000 | LitersPerSecond | R/W
9 | Indoor Pressure Filter level warning | HoldingRegister | 609 | Int | IntegerValue | I906 | 825 | 0 | 6000 | Pascals | R/W
9 | Economiser CO₂ Low Level | HoldingRegister | 610 | Int | IntegerValue | I907 | 826 | 0 | 1000 | PartsPerMillion | R/W
9 | Economiser CO₂ High Level | HoldingRegister | 611 | Int | IntegerValue | I908 | 827 | 0 | 1000 | PartsPerMillion | R/W
9 | BMS card Software version | InputRegister | 604 | Int | IntegerValue | I909 | 1226 | 0 | 32767 |  | R
9 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 605 | Int | IntegerValue | I910 | 1227 | 0 | 2 |  | R
9 | Air Filter Run Timer | InputRegister | 606 | Int | IntegerValue | I911 | 1228 | 0 | 10000 | Hours | R
9 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 607 | Int | IntegerValue | I912 | 1229 | 0 | 4 |  | R
9 | Indoor Airflow | InputRegister | 608 | Int | IntegerValue | I913 | 1230 | 0 | 6000 | LitersPerSecond | R
9 | Indoor Static Pressure | InputRegister | 609 | Int | IntegerValue | I914 | 1231 | 0 | 6000 | Pascals | R
9 | Measured CO₂ level | InputRegister | 610 | Int | IntegerValue | I915 | 1232 | 0 | 1000 | PartsPerMillion | R
9 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 611 | Int | IntegerValue | I916 | 1233 | 0 | 100 |  | R
9 | Error History Log, 1 error ago | InputRegister | 612 | Int | IntegerValue | I917 | 1234 | 0 | 100 |  | R
9 | Error History Log, 2 errors ago | InputRegister | 613 | Int | IntegerValue | I918 | 1235 | 0 | 100 |  | R
9 | Error History Log, 3 errors ago | InputRegister | 614 | Int | IntegerValue | I919 | 1236 | 0 | 100 |  | R
9 | Error History Log, 4 errors ago | InputRegister | 615 | Int | IntegerValue | I920 | 1237 | 0 | 100 |  | R
9 | Error History Log, 5 errors ago | InputRegister | 616 | Int | IntegerValue | I921 | 1238 | 0 | 100 |  | R
9 | Outdoor Unit 1 Model | InputRegister | 617 | Int | IntegerValue | I922 | 1239 | 0 | 32767 |  | R
9 | Outdoor Unit 1 Software version | InputRegister | 618 | Int | IntegerValue | I923 | 1240 | 0 | 32767 |  | R
9 | Compressor 1 Type | InputRegister | 619 | Int | IntegerValue | I924 | 1241 | 0 | 100 |  | R
9 | Compressor 1 Suction Pressure | InputRegister | 620 | Int | IntegerValue | I925 | 1242 | 0 | 6000 | KiloPascals | R
9 | Compressor 1 Discharge Pressure | InputRegister | 621 | Int | IntegerValue | I926 | 1243 | 0 | 6000 | KiloPascals | R
9 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 622 | Int | IntegerValue | I927 | 1244 | 0 | 3 |  | R
9 | Indoor Coil 1 Fan 1 Speed | InputRegister | 623 | Int | IntegerValue | I928 | 1245 | 0 | 9999 | RevolutionsPerMinute | R
9 | Generic Integer 1 | HoldingRegister | 612 | Int | IntegerValue | I929 | 828 |  |  |  | R/W
9 | Generic Integer 2 | HoldingRegister | 613 | Int | IntegerValue | I930 | 829 |  |  |  | R/W
9 | Generic Integer 3 | HoldingRegister | 614 | Int | IntegerValue | I931 | 830 |  |  |  | R/W
9 | Generic Integer 4 | HoldingRegister | 615 | Int | IntegerValue | I932 | 831 |  |  |  | R/W
9 | Generic Integer 5 | HoldingRegister | 616 | Int | IntegerValue | I933 | 832 |  |  |  | R/W

## Device 10
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
10 | Set Master Setpoint Temperature | HoldingRegister | 630 | Real | AnalogValue | A1001 | 833 | 16 | 30 | DegreesCelsius | R/W
10 | Economiser Temperature Difference | HoldingRegister | 634 | Real | AnalogValue | A1003 | 835 | 0 | 10 | DegreesCelsius | R/W
10 | Economiser Outside Min Temperature | HoldingRegister | 636 | Real | AnalogValue | A1004 | 836 | 0 | 22.5 | DegreesCelsius | R/W
10 | Economiser Outside Max Temperature | HoldingRegister | 638 | Real | AnalogValue | A1005 | 837 | 0 | 26 | DegreesCelsius | R/W
10 | Economiser Minimum Damper | HoldingRegister | 640 | Real | AnalogValue | A1006 | 838 | 0 | 10 | Volts | R/W
10 | Economiser Maximum Damper | HoldingRegister | 642 | Real | AnalogValue | A1007 | 839 | 0 | 10 | Volts | R/W
10 | Economiser Outside Max Moisture | HoldingRegister | 644 | Real | AnalogValue | A1008 | 840 | 0 | 100 | GramsPerKilogram | R/W
10 | Economiser Outside Max Dew Point | HoldingRegister | 646 | Real | AnalogValue | A1009 | 841 | 0 | 100 | DegreesCelsius | R/W
10 | Economiser Outside Max Enthalpy | HoldingRegister | 19 | Real | AnalogValue | A1010 | 526 | 0 | 100 | KilojoulesPerKilogram | R/W
10 | Economiser Enthalpy Delta | HoldingRegister | 648 | Real | AnalogValue | A1011 | 842 | 0 | 10 | KilojoulesPerKilogram | R/W
10 | Economiser CO₂ Minimum Damper | HoldingRegister | 650 | Real | AnalogValue | A1012 | 843 | 0 | 10 | Volts | R/W
10 | Economiser CO₂ Maximum Damper | HoldingRegister | 652 | Real | AnalogValue | A1013 | 844 | 0 | 10 | Volts | R/W
10 | Room Temperature | InputRegister | 632 | Real | AnalogValue | A1015 | 1247 | -99.9 | 99.9 | DegreesCelsius | R
10 | Indoor Room Temperature | InputRegister | 634 | Real | AnalogValue | A1016 | 1248 | -99.9 | 99.9 | DegreesCelsius | R
10 | Outside Temperature | InputRegister | 636 | Real | AnalogValue | A1017 | 1249 | -99.9 | 99.9 | DegreesCelsius | R
10 | Outside Air Temperature | InputRegister | 638 | Real | AnalogValue | A1018 | 1250 | -99.9 | 99.9 | DegreesCelsius | R
10 | Compressor 1 Suction Temperature | InputRegister | 640 | Real | AnalogValue | A1019 | 1251 | -999.9 | 999.9 | DegreesCelsius | R
10 | Compressor 1 Discharge Temperature | InputRegister | 642 | Real | AnalogValue | A1020 | 1252 | -999.9 | 999.9 | DegreesCelsius | R
10 | Compressor 1 Suction SuperHeat | InputRegister | 644 | Real | AnalogValue | A1021 | 1253 | -99.9 | 99.9 | DegreesCelsius | R
10 | Compressor 1 Suction SuperHeat Target | InputRegister | 646 | Real | AnalogValue | A1022 | 1254 | -99.9 | 99.9 | DegreesCelsius | R
10 | Outdoor Coil 1 Temperature | InputRegister | 648 | Real | AnalogValue | A1023 | 1255 |  |  | DegreesCelsius | R
10 | Indoor Coil 1 Temperature | InputRegister | 650 | Real | AnalogValue | A1024 | 1256 | -99.9 | 99.9 | DegreesCelsius | R
10 | Wall Control 1 Temperature | InputRegister | 652 | Real | AnalogValue | A1025 | 1257 | -99.9 | 99.9 | DegreesCelsius | R
10 | Wall Control 2 Temperature | InputRegister | 654 | Real | AnalogValue | A1026 | 1258 | -99.9 | 99.9 | DegreesCelsius | R
10 | Wall Control 3 Temperature | InputRegister | 656 | Real | AnalogValue | A1027 | 1259 | -99.9 | 99.9 | DegreesCelsius | R
10 | Auxillary Sensor 1 Temperature | InputRegister | 658 | Real | AnalogValue | A1028 | 1260 | -99.9 | 99.9 | DegreesCelsius | R
10 | Auxillary Sensor 2 Temperature | InputRegister | 660 | Real | AnalogValue | A1029 | 1261 | -99.9 | 99.9 | DegreesCelsius | R
10 | Auxillary Sensor 3 Temperature | InputRegister | 662 | Real | AnalogValue | A1030 | 1262 | -99.9 | 99.9 | DegreesCelsius | R
10 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 654 | Real | AnalogValue | A1031 | 845 | 0 | 100 | Percent | R/W
10 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 656 | Real | AnalogValue | A1032 | 846 | 0 | 100 | Percent | R/W
10 | Reduced Airflow Speed | HoldingRegister | 658 | Real | AnalogValue | A1033 | 847 | 0 | 100 | Percent | R/W
10 | Economiser Outside Max Humidity | HoldingRegister | 660 | Real | AnalogValue | A1034 | 848 | 0 | 100 | Percent | R/W
10 | Actual System Running Capacity | InputRegister | 664 | Real | AnalogValue | A1035 | 1263 | 0 | 100 | Percent | R
10 | Compressor 1 Demand | InputRegister | 666 | Real | AnalogValue | A1036 | 1264 | 0 | 100 | Percent | R
10 | Compressor 1 Speed | InputRegister | 668 | Real | AnalogValue | A1037 | 1265 | 0 | 100 | Percent | R
10 | Indoor Coil 1 Fan Speed | InputRegister | 670 | Real | AnalogValue | A1038 | 1266 | 0 | 100 | Percent | R
10 | Compressor 1 EEV position | InputRegister | 672 | Real | AnalogValue | A1039 | 1267 | 0 | 100 | Percent | R
10 | Generic Analog 01 | HoldingRegister | 662 | Real | AnalogValue | A1040 | 849 |  |  |  | R/W
10 | Generic Analog 02 | HoldingRegister | 664 | Real | AnalogValue | A1041 | 850 |  |  |  | R/W
10 | Generic Analog 03 | HoldingRegister | 666 | Real | AnalogValue | A1042 | 851 |  |  |  | R/W
10 | Generic Analog 04 | HoldingRegister | 668 | Real | AnalogValue | A1043 | 852 |  |  |  | R/W
10 | Generic Analog 05 | HoldingRegister | 670 | Real | AnalogValue | A1044 | 853 |  |  |  | R/W
10 | Turns the AC Off/On (0=Off, 1=On) | Coil | 270 | Bool | BinaryValue | D1001 | 244 |  |  |  | R/W
10 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 271 | Bool | BinaryValue | D1002 | 245 |  |  |  | R/W
10 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 272 | Bool | BinaryValue | D1003 | 246 |  |  |  | R/W
10 | Set Turbo Mode (0=Off, 1=On) | Coil | 273 | Bool | BinaryValue | D1004 | 247 |  |  |  | R/W
10 | Set Quiet Mode (0=Off, 1=On) | Coil | 274 | Bool | BinaryValue | D1005 | 248 |  |  |  | R/W
10 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 275 | Bool | BinaryValue | D1006 | 249 |  |  |  | R/W
10 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 278 | Bool | BinaryValue | D1009 | 252 |  |  |  | R/W
10 | Enable Economiser (0=Off, 1=On) | Coil | 279 | Bool | BinaryValue | D1010 | 253 |  |  |  | R/W
10 | Enable Humidity Control | Coil | 280 | Bool | BinaryValue | D1011 | 254 |  |  |  | R/W
10 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 281 | Bool | BinaryValue | D1012 | 255 |  |  |  | R/W
10 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 282 | Bool | BinaryValue | D1013 | 256 |  |  |  | R/W
10 | Enable CO₂ Control (0=Off, 1=On) | Coil | 283 | Bool | BinaryValue | D1014 | 257 |  |  |  | R/W
10 | Alarm Output (0=Off, 1=On) | DiscreteInput | 270 | Bool | BinaryValue | D1015 | 483 |  |  |  | R
10 | Air Filter Notification | DiscreteInput | 271 | Bool | BinaryValue | D1016 | 484 |  |  |  | R
10 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 274 | Bool | BinaryValue | D1019 | 487 |  |  |  | R
10 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 275 | Bool | BinaryValue | D1020 | 488 |  |  |  | R
10 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 276 | Bool | BinaryValue | D1021 | 489 |  |  |  | R
10 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 277 | Bool | BinaryValue | D1022 | 490 |  |  |  | R
10 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 278 | Bool | BinaryValue | D1023 | 491 |  |  |  | R
10 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 279 | Bool | BinaryValue | D1024 | 492 |  |  |  | R
10 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 280 | Bool | BinaryValue | D1025 | 493 |  |  |  | R
10 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 281 | Bool | BinaryValue | D1026 | 494 |  |  |  | R
10 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 282 | Bool | BinaryValue | D1027 | 495 |  |  |  | R
10 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 283 | Bool | BinaryValue | D1028 | 496 |  |  |  | R
10 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 284 | Bool | BinaryValue | D1029 | 497 |  |  |  | R
10 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 285 | Bool | BinaryValue | D1030 | 498 |  |  |  | R
10 | Compressor 1 Discharge Temp High | DiscreteInput | 286 | Bool | BinaryValue | D1031 | 499 |  |  |  | R
10 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 287 | Bool | BinaryValue | D1032 | 500 |  |  |  | R
10 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 288 | Bool | BinaryValue | D1033 | 501 |  |  |  | R
10 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 289 | Bool | BinaryValue | D1034 | 502 |  |  |  | R
10 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 290 | Bool | BinaryValue | D1035 | 503 |  |  |  | R
10 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 291 | Bool | BinaryValue | D1036 | 504 |  |  |  | R
10 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 292 | Bool | BinaryValue | D1037 | 505 |  |  |  | R
10 | Set zone 1 (0=Off, 1=On) | Coil | 284 | Bool | BinaryValue | D1038 | 258 |  |  |  | R/W
10 | Set zone 2 (0=Off, 1=On) | Coil | 285 | Bool | BinaryValue | D1039 | 259 |  |  |  | R/W
10 | Set zone 3 (0=Off, 1=On) | Coil | 286 | Bool | BinaryValue | D1040 | 260 |  |  |  | R/W
10 | Set zone 4 (0=Off, 1=On) | Coil | 287 | Bool | BinaryValue | D1041 | 261 |  |  |  | R/W
10 | Set zone 5 (0=Off, 1=On) | Coil | 288 | Bool | BinaryValue | D1042 | 262 |  |  |  | R/W
10 | Set zone 6 (0=Off, 1=On) | Coil | 289 | Bool | BinaryValue | D1043 | 263 |  |  |  | R/W
10 | Set zone 7 (0=Off, 1=On) | Coil | 290 | Bool | BinaryValue | D1044 | 264 |  |  |  | R/W
10 | Set zone 8 (0=Off, 1=On) | Coil | 291 | Bool | BinaryValue | D1045 | 265 |  |  |  | R/W
10 | Generic Digital 1 | Coil | 292 | Bool | BinaryValue | D1046 | 266 |  |  |  | R/W
10 | Generic Digital 2 | Coil | 293 | Bool | BinaryValue | D1047 | 267 |  |  |  | R/W
10 | Generic Digital 3 | Coil | 294 | Bool | BinaryValue | D1048 | 268 |  |  |  | R/W
10 | Generic Digital 4 | Coil | 295 | Bool | BinaryValue | D1049 | 269 |  |  |  | R/W
10 | Generic Digital 5 | Coil | 296 | Bool | BinaryValue | D1050 | 270 |  |  |  | R/W
10 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 672 | Int | IntegerValue | I1001 | 854 | 1 | 4 |  | R/W
10 | Set Air Filter Notification Timer | HoldingRegister | 673 | Int | IntegerValue | I1002 | 855 | 1 | 10000 | Hours | R/W
10 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 674 | Int | IntegerValue | I1003 | 856 | 1 | 4 |  | R/W
10 | Target Airflow | HoldingRegister | 675 | Int | IntegerValue | I1004 | 857 | 0 | 6000 | LitersPerSecond | R/W
10 | Enable Volumetric Airflow | HoldingRegister | 676 | Int | IntegerValue | I1005 | 858 | 0 | 6000 | LitersPerSecond | R/W
10 | Indoor Pressure Filter level warning | HoldingRegister | 677 | Int | IntegerValue | I1006 | 859 | 0 | 6000 | Pascals | R/W
10 | Economiser CO₂ Low Level | HoldingRegister | 678 | Int | IntegerValue | I1007 | 860 | 0 | 1000 | PartsPerMillion | R/W
10 | Economiser CO₂ High Level | HoldingRegister | 679 | Int | IntegerValue | I1008 | 861 | 0 | 1000 | PartsPerMillion | R/W
10 | BMS card Software version | InputRegister | 674 | Int | IntegerValue | I1009 | 1268 | 0 | 32767 |  | R
10 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 675 | Int | IntegerValue | I1010 | 1269 | 0 | 2 |  | R
10 | Air Filter Run Timer | InputRegister | 676 | Int | IntegerValue | I1011 | 1270 | 0 | 10000 | Hours | R
10 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 677 | Int | IntegerValue | I1012 | 1271 | 0 | 4 |  | R
10 | Indoor Airflow | InputRegister | 678 | Int | IntegerValue | I1013 | 1272 | 0 | 6000 | LitersPerSecond | R
10 | Indoor Static Pressure | InputRegister | 679 | Int | IntegerValue | I1014 | 1273 | 0 | 6000 | Pascals | R
10 | Measured CO₂ level | InputRegister | 680 | Int | IntegerValue | I1015 | 1274 | 0 | 1000 | PartsPerMillion | R
10 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 681 | Int | IntegerValue | I1016 | 1275 | 0 | 100 |  | R
10 | Error History Log, 1 error ago | InputRegister | 682 | Int | IntegerValue | I1017 | 1276 | 0 | 100 |  | R
10 | Error History Log, 2 errors ago | InputRegister | 683 | Int | IntegerValue | I1018 | 1277 | 0 | 100 |  | R
10 | Error History Log, 3 errors ago | InputRegister | 684 | Int | IntegerValue | I1019 | 1278 | 0 | 100 |  | R
10 | Error History Log, 4 errors ago | InputRegister | 685 | Int | IntegerValue | I1020 | 1279 | 0 | 100 |  | R
10 | Error History Log, 5 errors ago | InputRegister | 686 | Int | IntegerValue | I1021 | 1280 | 0 | 100 |  | R
10 | Outdoor Unit 1 Model | InputRegister | 687 | Int | IntegerValue | I1022 | 1281 | 0 | 32767 |  | R
10 | Outdoor Unit 1 Software version | InputRegister | 688 | Int | IntegerValue | I1023 | 1282 | 0 | 32767 |  | R
10 | Compressor 1 Type | InputRegister | 689 | Int | IntegerValue | I1024 | 1283 | 0 | 100 |  | R
10 | Compressor 1 Suction Pressure | InputRegister | 690 | Int | IntegerValue | I1025 | 1284 | 0 | 6000 | KiloPascals | R
10 | Compressor 1 Discharge Pressure | InputRegister | 691 | Int | IntegerValue | I1026 | 1285 | 0 | 6000 | KiloPascals | R
10 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 692 | Int | IntegerValue | I1027 | 1286 | 0 | 3 |  | R
10 | Indoor Coil 1 Fan 1 Speed | InputRegister | 693 | Int | IntegerValue | I1028 | 1287 | 0 | 9999 | RevolutionsPerMinute | R
10 | Generic Integer 1 | HoldingRegister | 680 | Int | IntegerValue | I1029 | 862 |  |  |  | R/W
10 | Generic Integer 2 | HoldingRegister | 681 | Int | IntegerValue | I1030 | 863 |  |  |  | R/W
10 | Generic Integer 3 | HoldingRegister | 682 | Int | IntegerValue | I1031 | 864 |  |  |  | R/W
10 | Generic Integer 4 | HoldingRegister | 683 | Int | IntegerValue | I1032 | 865 |  |  |  | R/W
10 | Generic Integer 5 | HoldingRegister | 684 | Int | IntegerValue | I1033 | 866 |  |  |  | R/W

## Device 11
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
11 | Device 11 Universal I/O - U2 | InputRegister | 702 | Real | AnalogValue | A1102 | 1289 |  |  |  | R
11 | Device 11 Universal I/O - U3 | InputRegister | 704 | Real | AnalogValue | A1103 | 1290 |  |  |  | R
11 | Device 11 Universal I/O - U4 | InputRegister | 706 | Real | AnalogValue | A1104 | 1291 |  |  |  | R
11 | Device 11 Universal I/O - U5 | InputRegister | 708 | Real | AnalogValue | A1105 | 1292 |  |  |  | R
11 | Device 11 Universal I/O - U6 | HoldingRegister | 700 | Real | AnalogValue | A1106 | 867 |  |  |  | R/W
11 | Device 11 Universal I/O - U7 | InputRegister | 712 | Real | AnalogValue | A1107 | 1293 |  |  |  | R
11 | Device 11 Universal I/O - U8 | InputRegister | 714 | Real | AnalogValue | A1108 | 1294 |  |  |  | R
11 | Device 11 Universal I/O - U9 | InputRegister | 716 | Real | AnalogValue | A1109 | 1295 |  |  |  | R
11 | Device 11 Universal I/O - U10 | InputRegister | 718 | Real | AnalogValue | A1110 | 1296 |  |  |  | R
11 | Device 11 relay 1 | Coil | 300 | Bool | BinaryValue | D1101 | 271 |  |  |  | R/W
11 | Device 11 relay 2 | Coil | 301 | Bool | BinaryValue | D1102 | 272 |  |  |  | R/W
11 | Device 11 relay 3 | Coil | 302 | Bool | BinaryValue | D1103 | 273 |  |  |  | R/W
11 | Device 11 relay 4 | Coil | 303 | Bool | BinaryValue | D1104 | 274 |  |  |  | R/W
11 | Device 11 relay 5 | Coil | 304 | Bool | BinaryValue | D1105 | 275 |  |  |  | R/W
11 | Device 11 relay 6 General Alarm | DiscreteInput | 300 | Bool | BinaryValue | D1106 | 506 |  |  |  | R
11 | Device 11 Universal I/O - U1 | DiscreteInput | 301 | Bool | BinaryValue | D1111 | 507 |  |  |  | R
11 | Device 11 Universal I/O - U2 | DiscreteInput | 302 | Bool | BinaryValue | D1112 | 508 |  |  |  | R
11 | Device 11 Universal I/O - U3 | DiscreteInput | 303 | Bool | BinaryValue | D1113 | 509 |  |  |  | R
11 | Device 11 Universal I/O - U4 | DiscreteInput | 304 | Bool | BinaryValue | D1114 | 510 |  |  |  | R
11 | Device 11 Universal I/O - U5 | DiscreteInput | 305 | Bool | BinaryValue | D1115 | 511 |  |  |  | R
11 | Device 11 Universal I/O - U7 | DiscreteInput | 307 | Bool | BinaryValue | D1117 | 513 |  |  |  | R
11 | Device 11 Universal I/O - U8 | DiscreteInput | 308 | Bool | BinaryValue | D1118 | 514 |  |  |  | R
11 | Device 11 Universal I/O - U9 | DiscreteInput | 309 | Bool | BinaryValue | D1119 | 515 |  |  |  | R
11 | Device 11 Universal I/O - U10 | DiscreteInput | 310 | Bool | BinaryValue | D1120 | 516 |  |  |  | R

## All
Device | Variable Description | Modbus |  |  | BACnet |  |  | Shared
|  | Type | Index | DataType | Type | Variable Name | ObjInstance | Min | Max | UoM | Direction
1 | Set Master Setpoint Temperature | HoldingRegister | 1 | Real | AnalogValue | A101 | 517 | 16 | 30 | DegreesCelsius | R/W
1 | Economiser Temperature Difference | HoldingRegister | 5 | Real | AnalogValue | A103 | 519 | 0 | 10 | DegreesCelsius | R/W
1 | Economiser Outside Min Temperature | HoldingRegister | 7 | Real | AnalogValue | A104 | 520 | 0 | 22.5 | DegreesCelsius | R/W
1 | Economiser Outside Max Temperature | HoldingRegister | 9 | Real | AnalogValue | A105 | 521 | 0 | 26 | DegreesCelsius | R/W
1 | Economiser Minimum Damper | HoldingRegister | 11 | Real | AnalogValue | A106 | 522 | 0 | 10 | Volts | R/W
1 | Economiser Maximum Damper | HoldingRegister | 13 | Real | AnalogValue | A107 | 523 | 0 | 10 | Volts | R/W
1 | Economiser Outside Max Moisture | HoldingRegister | 15 | Real | AnalogValue | A108 | 524 | 0 | 100 | GramsPerKilogram | R/W
1 | Economiser Outside Max Dew Point | HoldingRegister | 17 | Real | AnalogValue | A109 | 525 | 0 | 100 | DegreesCelsius | R/W
1 | Economiser Outside Max Enthalpy | HoldingRegister | 21 | Real | AnalogValue | A110 | 527 | 0 | 100 | KilojoulesPerKilogram | R/W
1 | Economiser Enthalpy Delta | HoldingRegister | 23 | Real | AnalogValue | A111 | 528 | 0 | 10 | KilojoulesPerKilogram | R/W
1 | Economiser CO₂ Minimum Damper | HoldingRegister | 25 | Real | AnalogValue | A112 | 529 | 0 | 10 | Volts | R/W
1 | Economiser CO₂ Maximum Damper | HoldingRegister | 27 | Real | AnalogValue | A113 | 530 | 0 | 10 | Volts | R/W
1 | Room Temperature | InputRegister | 2 | Real | AnalogValue | A115 | 869 | -99.9 | 99.9 | DegreesCelsius | R
1 | Indoor Room Temperature | InputRegister | 4 | Real | AnalogValue | A116 | 870 | -99.9 | 99.9 | DegreesCelsius | R
1 | Outside Temperature | InputRegister | 6 | Real | AnalogValue | A117 | 871 | -99.9 | 99.9 | DegreesCelsius | R
1 | Outside Air Temperature | InputRegister | 8 | Real | AnalogValue | A118 | 872 | -99.9 | 99.9 | DegreesCelsius | R
1 | Compressor 1 Suction Temperature | InputRegister | 10 | Real | AnalogValue | A119 | 873 | -999.9 | 999.9 | DegreesCelsius | R
1 | Compressor 1 Discharge Temperature | InputRegister | 12 | Real | AnalogValue | A120 | 874 | -999.9 | 999.9 | DegreesCelsius | R
1 | Compressor 1 Suction SuperHeat | InputRegister | 14 | Real | AnalogValue | A121 | 875 | -99.9 | 99.9 | DegreesCelsius | R
1 | Compressor 1 Suction SuperHeat Target | InputRegister | 16 | Real | AnalogValue | A122 | 876 | -99.9 | 99.9 | DegreesCelsius | R
1 | Outdoor Coil 1 Temperature | InputRegister | 18 | Real | AnalogValue | A123 | 877 | -99.9 | 99.9 | DegreesCelsius | R
1 | Indoor Coil 1 Temperature | InputRegister | 20 | Real | AnalogValue | A124 | 878 | -99.9 | 99.9 | DegreesCelsius | R
1 | Wall Control 1 Temperature | InputRegister | 22 | Real | AnalogValue | A125 | 879 | -99.9 | 99.9 | DegreesCelsius | R
1 | Wall Control 2 Temperature | InputRegister | 24 | Real | AnalogValue | A126 | 880 | -99.9 | 99.9 | DegreesCelsius | R
1 | Wall Control 3 Temperature | InputRegister | 26 | Real | AnalogValue | A127 | 881 | -99.9 | 99.9 | DegreesCelsius | R
1 | Auxillary Sensor 1 Temperature | InputRegister | 28 | Real | AnalogValue | A128 | 882 | -99.9 | 99.9 | DegreesCelsius | R
1 | Auxillary Sensor 2 Temperature | InputRegister | 30 | Real | AnalogValue | A129 | 883 | -99.9 | 99.9 | DegreesCelsius | R
1 | Auxillary Sensor 3 Temperature | InputRegister | 32 | Real | AnalogValue | A130 | 884 | -99.9 | 99.9 | DegreesCelsius | R
1 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 29 | Real | AnalogValue | A131 | 531 | 0 | 100 | Percent | R/W
1 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 31 | Real | AnalogValue | A132 | 532 | 0 | 100 | Percent | R/W
1 | Reduced Airflow Speed | HoldingRegister | 33 | Real | AnalogValue | A133 | 533 | 0 | 100 | Percent | R/W
1 | Economiser Outside Max Humidity | HoldingRegister | 35 | Real | AnalogValue | A134 | 534 | 0 | 100 | Percent | R/W
1 | Actual System Running Capacity | InputRegister | 34 | Real | AnalogValue | A135 | 885 | 0 | 100 | Percent | R
1 | Compressor 1 Demand | InputRegister | 36 | Real | AnalogValue | A136 | 886 | 0 | 100 | Percent | R
1 | Compressor 1 Speed | InputRegister | 38 | Real | AnalogValue | A137 | 887 | 0 | 100 | Percent | R
1 | Indoor Coil 1 Fan Speed | InputRegister | 40 | Real | AnalogValue | A138 | 888 | 0 | 100 | Percent | R
1 | Compressor 1 EEV position | InputRegister | 42 | Real | AnalogValue | A139 | 889 | 0 | 100 | Percent | R
1 | Generic Analog 01 | HoldingRegister | 37 | Real | AnalogValue | A140 | 535 |  |  |  | R/W
1 | Generic Analog 02 | HoldingRegister | 39 | Real | AnalogValue | A141 | 536 |  |  |  | R/W
1 | Generic Analog 03 | HoldingRegister | 41 | Real | AnalogValue | A142 | 537 |  |  |  | R/W
1 | Generic Analog 04 | HoldingRegister | 43 | Real | AnalogValue | A143 | 538 |  |  |  | R/W
1 | Generic Analog 05 | HoldingRegister | 45 | Real | AnalogValue | A144 | 539 |  |  |  | R/W
1 | Turns the AC Off/On (0=Off, 1=On) | Coil | 0 | Bool | BinaryValue | D101 | 1 |  |  |  | R/W
1 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 1 | Bool | BinaryValue | D102 | 2 |  |  |  | R/W
1 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 2 | Bool | BinaryValue | D103 | 3 |  |  |  | R/W
1 | Set Turbo Mode (0=Off, 1=On) | Coil | 3 | Bool | BinaryValue | D104 | 4 |  |  |  | R/W
1 | Set Quiet Mode (0=Off, 1=On) | Coil | 4 | Bool | BinaryValue | D105 | 5 |  |  |  | R/W
1 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 5 | Bool | BinaryValue | D106 | 6 |  |  |  | R/W
1 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 8 | Bool | BinaryValue | D109 | 9 |  |  |  | R/W
1 | Enable Economiser (0=Off, 1=On) | Coil | 9 | Bool | BinaryValue | D110 | 10 |  |  |  | R/W
1 | Enable Humidity Control | Coil | 10 | Bool | BinaryValue | D111 | 11 |  |  |  | R/W
1 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 11 | Bool | BinaryValue | D112 | 12 |  |  |  | R/W
1 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 12 | Bool | BinaryValue | D113 | 13 |  |  |  | R/W
1 | Enable CO₂ Control (0=Off, 1=On) | Coil | 13 | Bool | BinaryValue | D114 | 14 |  |  |  | R/W
1 | Alarm Output (0=Off, 1=On) | DiscreteInput | 0 | Bool | BinaryValue | D115 | 276 |  |  |  | R
1 | Air Filter Notification | DiscreteInput | 1 | Bool | BinaryValue | D116 | 277 |  |  |  | R
1 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 4 | Bool | BinaryValue | D119 | 280 |  |  |  | R
1 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 5 | Bool | BinaryValue | D120 | 281 |  |  |  | R
1 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 6 | Bool | BinaryValue | D121 | 282 |  |  |  | R
1 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 7 | Bool | BinaryValue | D122 | 283 |  |  |  | R
1 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 8 | Bool | BinaryValue | D123 | 284 |  |  |  | R
1 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 9 | Bool | BinaryValue | D124 | 285 |  |  |  | R
1 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 10 | Bool | BinaryValue | D125 | 286 |  |  |  | R
1 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 11 | Bool | BinaryValue | D126 | 287 |  |  |  | R
1 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 12 | Bool | BinaryValue | D127 | 288 |  |  |  | R
1 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 13 | Bool | BinaryValue | D128 | 289 |  |  |  | R
1 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 14 | Bool | BinaryValue | D129 | 290 |  |  |  | R
1 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 15 | Bool | BinaryValue | D130 | 291 |  |  |  | R
1 | Compressor 1 Discharge Temp High | DiscreteInput | 16 | Bool | BinaryValue | D131 | 292 |  |  |  | R
1 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 17 | Bool | BinaryValue | D132 | 293 |  |  |  | R
1 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 18 | Bool | BinaryValue | D133 | 294 |  |  |  | R
1 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 19 | Bool | BinaryValue | D134 | 295 |  |  |  | R
1 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 20 | Bool | BinaryValue | D135 | 296 |  |  |  | R
1 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 21 | Bool | BinaryValue | D136 | 297 |  |  |  | R
1 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 22 | Bool | BinaryValue | D137 | 298 |  |  |  | R
1 | Set zone 1 (0=Off, 1=On) | Coil | 14 | Bool | BinaryValue | D138 | 15 |  |  |  | R/W
1 | Set zone 2 (0=Off, 1=On) | Coil | 15 | Bool | BinaryValue | D139 | 16 |  |  |  | R/W
1 | Set zone 3 (0=Off, 1=On) | Coil | 16 | Bool | BinaryValue | D140 | 17 |  |  |  | R/W
1 | Set zone 4 (0=Off, 1=On) | Coil | 17 | Bool | BinaryValue | D141 | 18 |  |  |  | R/W
1 | Set zone 5 (0=Off, 1=On) | Coil | 18 | Bool | BinaryValue | D142 | 19 |  |  |  | R/W
1 | Set zone 6 (0=Off, 1=On) | Coil | 19 | Bool | BinaryValue | D143 | 20 |  |  |  | R/W
1 | Set zone 7 (0=Off, 1=On) | Coil | 20 | Bool | BinaryValue | D144 | 21 |  |  |  | R/W
1 | Set zone 8 (0=Off, 1=On) | Coil | 21 | Bool | BinaryValue | D145 | 22 |  |  |  | R/W
1 | Generic Digital 1 | Coil | 22 | Bool | BinaryValue | D146 | 23 |  |  |  | R/W
1 | Generic Digital 2 | Coil | 23 | Bool | BinaryValue | D147 | 24 |  |  |  | R/W
1 | Generic Digital 3 | Coil | 24 | Bool | BinaryValue | D148 | 25 |  |  |  | R/W
1 | Generic Digital 4 | Coil | 25 | Bool | BinaryValue | D149 | 26 |  |  |  | R/W
1 | Generic Digital 5 | Coil | 26 | Bool | BinaryValue | D150 | 27 |  |  |  | R/W
1 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 47 | Int | IntegerValue | I101 | 540 | 1 | 4 |  | R/W
1 | Set Air Filter Notification Timer | HoldingRegister | 48 | Int | IntegerValue | I102 | 541 | 1 | 10000 | Hours | R/W
1 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 49 | Int | IntegerValue | I103 | 542 | 1 | 4 |  | R/W
1 | Target Airflow | HoldingRegister | 50 | Int | IntegerValue | I104 | 543 | 0 | 6000 | LitersPerSecond | R/W
1 | Enable Volumetric Airflow | HoldingRegister | 51 | Int | IntegerValue | I105 | 544 | 0 | 6000 | LitersPerSecond | R/W
1 | Indoor Pressure Filter level warning | HoldingRegister | 52 | Int | IntegerValue | I106 | 545 | 0 | 6000 | Pascals | R/W
1 | Economiser CO₂ Low Level | HoldingRegister | 53 | Int | IntegerValue | I107 | 546 | 0 | 1000 | PartsPerMillion | R/W
1 | Economiser CO₂ High Level | HoldingRegister | 54 | Int | IntegerValue | I108 | 547 | 0 | 1000 | PartsPerMillion | R/W
1 | BMS card Software version | InputRegister | 44 | Int | IntegerValue | I109 | 890 | 0 | 32767 |  | R
1 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 45 | Int | IntegerValue | I110 | 891 | 0 | 2 |  | R
1 | Air Filter Run Timer | InputRegister | 46 | Int | IntegerValue | I111 | 892 | 0 | 10000 | Hours | R
1 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 47 | Int | IntegerValue | I112 | 893 | 0 | 4 |  | R
1 | Indoor Airflow | InputRegister | 48 | Int | IntegerValue | I113 | 894 | 0 | 6000 | LitersPerSecond | R
1 | Indoor Static Pressure | InputRegister | 49 | Int | IntegerValue | I114 | 895 | 0 | 6000 | Pascals | R
1 | Measured CO₂ level | InputRegister | 50 | Int | IntegerValue | I115 | 896 | 0 | 1000 | PartsPerMillion | R
1 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 51 | Int | IntegerValue | I116 | 897 | 0 | 100 |  | R
1 | Error History Log, 1 error ago | InputRegister | 52 | Int | IntegerValue | I117 | 898 | 0 | 100 |  | R
1 | Error History Log, 2 errors ago | InputRegister | 53 | Int | IntegerValue | I118 | 899 | 0 | 100 |  | R
1 | Error History Log, 3 errors ago | InputRegister | 54 | Int | IntegerValue | I119 | 900 | 0 | 100 |  | R
1 | Error History Log, 4 errors ago | InputRegister | 55 | Int | IntegerValue | I120 | 901 | 0 | 100 |  | R
1 | Error History Log, 5 errors ago | InputRegister | 56 | Int | IntegerValue | I121 | 902 | 0 | 100 |  | R
1 | Outdoor Unit 1 Model | InputRegister | 57 | Int | IntegerValue | I122 | 903 | 0 | 32767 |  | R
1 | Outdoor Unit 1 Software version | InputRegister | 58 | Int | IntegerValue | I123 | 904 | 0 | 32767 |  | R
1 | Compressor 1 Type | InputRegister | 59 | Int | IntegerValue | I124 | 905 | 0 | 100 |  | R
1 | Compressor 1 Suction Pressure | InputRegister | 60 | Int | IntegerValue | I125 | 906 | 0 | 6000 | KiloPascals | R
1 | Compressor 1 Discharge Pressure | InputRegister | 61 | Int | IntegerValue | I126 | 907 | 0 | 6000 | KiloPascals | R
1 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 62 | Int | IntegerValue | I127 | 908 | 0 | 3 |  | R
1 | Indoor Coil 1 Fan 1 Speed | InputRegister | 63 | Int | IntegerValue | I128 | 909 | 0 | 9999 | RevolutionsPerMinute | R
1 | Generic Integer 1 | HoldingRegister | 55 | Int | IntegerValue | I129 | 548 |  |  |  | R/W
1 | Generic Integer 2 | HoldingRegister | 56 | Int | IntegerValue | I130 | 549 |  |  |  | R/W
1 | Generic Integer 3 | HoldingRegister | 57 | Int | IntegerValue | I131 | 550 |  |  |  | R/W
1 | Generic Integer 4 | HoldingRegister | 58 | Int | IntegerValue | I132 | 551 |  |  |  | R/W
1 | Generic Integer 5 | HoldingRegister | 59 | Int | IntegerValue | I133 | 552 |  |  |  | R/W
2 | Set Master Setpoint Temperature | HoldingRegister | 70 | Real | AnalogValue | A201 | 553 | 16 | 30 | DegreesCelsius | R/W
2 | Economiser Temperature Difference | HoldingRegister | 74 | Real | AnalogValue | A203 | 555 | 0 | 10 | DegreesCelsius | R/W
2 | Economiser Outside Min Temperature | HoldingRegister | 76 | Real | AnalogValue | A204 | 556 | 0 | 22.5 | DegreesCelsius | R/W
2 | Economiser Outside Max Temperature | HoldingRegister | 78 | Real | AnalogValue | A205 | 557 | 0 | 26 | DegreesCelsius | R/W
2 | Economiser Minimum Damper | HoldingRegister | 80 | Real | AnalogValue | A206 | 558 | 0 | 10 | Volts | R/W
2 | Economiser Maximum Damper | HoldingRegister | 82 | Real | AnalogValue | A207 | 559 | 0 | 10 | Volts | R/W
2 | Economiser Outside Max Moisture | HoldingRegister | 84 | Real | AnalogValue | A208 | 560 | 0 | 100 | GramsPerKilogram | R/W
2 | Economiser Outside Max Dew Point | HoldingRegister | 86 | Real | AnalogValue | A209 | 561 | 0 | 100 | DegreesCelsius | R/W
2 | Economiser Outside Max Enthalpy | HoldingRegister | 88 | Real | AnalogValue | A210 | 562 | 0 | 100 | KilojoulesPerKilogram | R/W
2 | Economiser Enthalpy Delta | HoldingRegister | 90 | Real | AnalogValue | A211 | 563 | 0 | 10 | KilojoulesPerKilogram | R/W
2 | Economiser CO₂ Minimum Damper | HoldingRegister | 92 | Real | AnalogValue | A212 | 564 | 0 | 10 | Volts | R/W
2 | Economiser CO₂ Maximum Damper | HoldingRegister | 94 | Real | AnalogValue | A213 | 565 | 0 | 10 | Volts | R/W
2 | Room Temperature | InputRegister | 72 | Real | AnalogValue | A215 | 911 | -99.9 | 99.9 | DegreesCelsius | R
2 | Indoor Room Temperature | InputRegister | 74 | Real | AnalogValue | A216 | 912 | -99.9 | 99.9 | DegreesCelsius | R
2 | Outside Temperature | InputRegister | 76 | Real | AnalogValue | A217 | 913 | -99.9 | 99.9 | DegreesCelsius | R
2 | Outside Air Temperature | InputRegister | 78 | Real | AnalogValue | A218 | 914 | -99.9 | 99.9 | DegreesCelsius | R
2 | Compressor 1 Suction Temperature | InputRegister | 80 | Real | AnalogValue | A219 | 915 | -999.9 | 999.9 | DegreesCelsius | R
2 | Compressor 1 Discharge Temperature | InputRegister | 82 | Real | AnalogValue | A220 | 916 | -999.9 | 999.9 | DegreesCelsius | R
2 | Compressor 1 Suction SuperHeat | InputRegister | 84 | Real | AnalogValue | A221 | 917 | -99.9 | 99.9 | DegreesCelsius | R
2 | Compressor 1 Suction SuperHeat Target | InputRegister | 86 | Real | AnalogValue | A222 | 918 | -99.9 | 99.9 | DegreesCelsius | R
2 | Outdoor Coil 1 Temperature | InputRegister | 88 | Real | AnalogValue | A223 | 919 | -99.9 | 99.9 | DegreesCelsius | R
2 | Indoor Coil 1 Temperature | InputRegister | 90 | Real | AnalogValue | A224 | 920 | -99.9 | 99.9 | DegreesCelsius | R
2 | Wall Control 1 Temperature | InputRegister | 92 | Real | AnalogValue | A225 | 921 | -99.9 | 99.9 | DegreesCelsius | R
2 | Wall Control 2 Temperature | InputRegister | 94 | Real | AnalogValue | A226 | 922 | -99.9 | 99.9 | DegreesCelsius | R
2 | Wall Control 3 Temperature | InputRegister | 96 | Real | AnalogValue | A227 | 923 | -99.9 | 99.9 | DegreesCelsius | R
2 | Auxillary Sensor 1 Temperature | InputRegister | 98 | Real | AnalogValue | A228 | 924 | -99.9 | 99.9 | DegreesCelsius | R
2 | Auxillary Sensor 2 Temperature | InputRegister | 100 | Real | AnalogValue | A229 | 925 | -99.9 | 99.9 | DegreesCelsius | R
2 | Auxillary Sensor 3 Temperature | InputRegister | 102 | Real | AnalogValue | A230 | 926 | -99.9 | 99.9 | DegreesCelsius | R
2 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 96 | Real | AnalogValue | A231 | 566 | 0 | 100 | Percent | R/W
2 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 98 | Real | AnalogValue | A232 | 567 | 0 | 100 | Percent | R/W
2 | Reduced Airflow Speed | HoldingRegister | 100 | Real | AnalogValue | A233 | 568 | 0 | 100 | Percent | R/W
2 | Economiser Outside Max Humidity | HoldingRegister | 102 | Real | AnalogValue | A234 | 569 | 0 | 100 | Percent | R/W
2 | Actual System Running Capacity | InputRegister | 104 | Real | AnalogValue | A235 | 927 | 0 | 100 | Percent | R
2 | Compressor 1 Demand | InputRegister | 106 | Real | AnalogValue | A236 | 928 | 0 | 100 | Percent | R
2 | Compressor 1 Speed | InputRegister | 108 | Real | AnalogValue | A237 | 929 | 0 | 100 | Percent | R
2 | Indoor Coil 1 Fan Speed | InputRegister | 110 | Real | AnalogValue | A238 | 930 | 0 | 100 | Percent | R
2 | Compressor 1 EEV position | InputRegister | 112 | Real | AnalogValue | A239 | 931 | 0 | 100 | Percent | R
2 | Generic Analog 01 | HoldingRegister | 104 | Real | AnalogValue | A240 | 570 |  |  |  | R/W
2 | Generic Analog 02 | HoldingRegister | 106 | Real | AnalogValue | A241 | 571 |  |  |  | R/W
2 | Generic Analog 03 | HoldingRegister | 108 | Real | AnalogValue | A242 | 572 |  |  |  | R/W
2 | Generic Analog 04 | HoldingRegister | 110 | Real | AnalogValue | A243 | 573 |  |  |  | R/W
2 | Generic Analog 05 | HoldingRegister | 112 | Real | AnalogValue | A244 | 574 |  |  |  | R/W
2 | Turns the AC Off/On (0=Off, 1=On) | Coil | 30 | Bool | BinaryValue | D201 | 28 |  |  |  | R/W
2 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 31 | Bool | BinaryValue | D202 | 29 |  |  |  | R/W
2 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 32 | Bool | BinaryValue | D203 | 30 |  |  |  | R/W
2 | Set Turbo Mode (0=Off, 1=On) | Coil | 34 | Bool | BinaryValue | D204 | 31 |  |  |  | R/W
2 | Set Quiet Mode (0=Off, 1=On) | Coil | 35 | Bool | BinaryValue | D205 | 32 |  |  |  | R/W
2 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 36 | Bool | BinaryValue | D206 | 33 |  |  |  | R/W
2 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 39 | Bool | BinaryValue | D209 | 36 |  |  |  | R/W
2 | Enable Economiser (0=Off, 1=On) | Coil | 40 | Bool | BinaryValue | D210 | 37 |  |  |  | R/W
2 | Enable Humidity Control | Coil | 41 | Bool | BinaryValue | D211 | 38 |  |  |  | R/W
2 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 42 | Bool | BinaryValue | D212 | 39 |  |  |  | R/W
2 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 43 | Bool | BinaryValue | D213 | 40 |  |  |  | R/W
2 | Enable CO₂ Control (0=Off, 1=On) | Coil | 44 | Bool | BinaryValue | D214 | 41 |  |  |  | R/W
2 | Alarm Output (0=Off, 1=On) | DiscreteInput | 30 | Bool | BinaryValue | D215 | 299 |  |  |  | R
2 | Air Filter Notification | DiscreteInput | 31 | Bool | BinaryValue | D216 | 300 |  |  |  | R
2 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 34 | Bool | BinaryValue | D219 | 303 |  |  |  | R
2 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 35 | Bool | BinaryValue | D220 | 304 |  |  |  | R
2 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 36 | Bool | BinaryValue | D221 | 305 |  |  |  | R
2 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 37 | Bool | BinaryValue | D222 | 306 |  |  |  | R
2 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 38 | Bool | BinaryValue | D223 | 307 |  |  |  | R
2 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 39 | Bool | BinaryValue | D224 | 308 |  |  |  | R
2 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 40 | Bool | BinaryValue | D225 | 309 |  |  |  | R
2 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 41 | Bool | BinaryValue | D226 | 310 |  |  |  | R
2 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 42 | Bool | BinaryValue | D227 | 311 |  |  |  | R
2 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 43 | Bool | BinaryValue | D228 | 312 |  |  |  | R
2 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 44 | Bool | BinaryValue | D229 | 313 |  |  |  | R
2 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 45 | Bool | BinaryValue | D230 | 314 |  |  |  | R
2 | Compressor 1 Discharge Temp High | DiscreteInput | 46 | Bool | BinaryValue | D231 | 315 |  |  |  | R
2 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 47 | Bool | BinaryValue | D232 | 316 |  |  |  | R
2 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 48 | Bool | BinaryValue | D233 | 317 |  |  |  | R
2 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 49 | Bool | BinaryValue | D234 | 318 |  |  |  | R
2 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 50 | Bool | BinaryValue | D235 | 319 |  |  |  | R
2 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 51 | Bool | BinaryValue | D236 | 320 |  |  |  | R
2 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 52 | Bool | BinaryValue | D237 | 321 |  |  |  | R
2 | Set zone 1 (0=Off, 1=On) | Coil | 45 | Bool | BinaryValue | D238 | 42 |  |  |  | R/W
2 | Set zone 2 (0=Off, 1=On) | Coil | 46 | Bool | BinaryValue | D239 | 43 |  |  |  | R/W
2 | Set zone 3 (0=Off, 1=On) | Coil | 47 | Bool | BinaryValue | D240 | 44 |  |  |  | R/W
2 | Set zone 4 (0=Off, 1=On) | Coil | 48 | Bool | BinaryValue | D241 | 45 |  |  |  | R/W
2 | Set zone 5 (0=Off, 1=On) | Coil | 49 | Bool | BinaryValue | D242 | 46 |  |  |  | R/W
2 | Set zone 6 (0=Off, 1=On) | Coil | 50 | Bool | BinaryValue | D243 | 47 |  |  |  | R/W
2 | Set zone 7 (0=Off, 1=On) | Coil | 51 | Bool | BinaryValue | D244 | 48 |  |  |  | R/W
2 | Set zone 8 (0=Off, 1=On) | Coil | 52 | Bool | BinaryValue | D245 | 49 |  |  |  | R/W
2 | Generic Digital 1 | Coil | 53 | Bool | BinaryValue | D246 | 50 |  |  |  | R/W
2 | Generic Digital 2 | Coil | 54 | Bool | BinaryValue | D247 | 51 |  |  |  | R/W
2 | Generic Digital 3 | Coil | 55 | Bool | BinaryValue | D248 | 52 |  |  |  | R/W
2 | Generic Digital 4 | Coil | 56 | Bool | BinaryValue | D249 | 53 |  |  |  | R/W
2 | Generic Digital 5 | Coil | 57 | Bool | BinaryValue | D250 | 54 |  |  |  | R/W
2 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 114 | Int | IntegerValue | I201 | 575 | 1 | 4 |  | R/W
2 | Set Air Filter Notification Timer | HoldingRegister | 115 | Int | IntegerValue | I202 | 576 | 1 | 10000 | Hours | R/W
2 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 116 | Int | IntegerValue | I203 | 577 | 1 | 4 |  | R/W
2 | Target Airflow | HoldingRegister | 117 | Int | IntegerValue | I204 | 578 | 0 | 6000 | LitersPerSecond | R/W
2 | Enable Volumetric Airflow | HoldingRegister | 118 | Int | IntegerValue | I205 | 579 | 0 | 6000 | LitersPerSecond | R/W
2 | Indoor Pressure Filter level warning | HoldingRegister | 119 | Int | IntegerValue | I206 | 580 | 0 | 6000 | Pascals | R/W
2 | Economiser CO₂ Low Level | HoldingRegister | 120 | Int | IntegerValue | I207 | 581 | 0 | 1000 | PartsPerMillion | R/W
2 | Economiser CO₂ High Level | HoldingRegister | 121 | Int | IntegerValue | I208 | 582 | 0 | 1000 | PartsPerMillion | R/W
2 | BMS card Software version | InputRegister | 114 | Int | IntegerValue | I209 | 932 | 0 | 32767 |  | R
2 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 115 | Int | IntegerValue | I210 | 933 | 0 | 2 |  | R
2 | Air Filter Run Timer | InputRegister | 116 | Int | IntegerValue | I211 | 934 | 0 | 10000 | Hours | R
2 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 117 | Int | IntegerValue | I212 | 935 | 0 | 4 |  | R
2 | Indoor Airflow | InputRegister | 118 | Int | IntegerValue | I213 | 936 | 0 | 6000 | LitersPerSecond | R
2 | Indoor Static Pressure | InputRegister | 119 | Int | IntegerValue | I214 | 937 | 0 | 6000 | Pascals | R
2 | Measured CO₂ level | InputRegister | 120 | Int | IntegerValue | I215 | 938 | 0 | 1000 | PartsPerMillion | R
2 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 121 | Int | IntegerValue | I216 | 939 | 0 | 100 |  | R
2 | Error History Log, 1 error ago | InputRegister | 122 | Int | IntegerValue | I217 | 940 | 0 | 100 |  | R
2 | Error History Log, 2 errors ago | InputRegister | 123 | Int | IntegerValue | I218 | 941 | 0 | 100 |  | R
2 | Error History Log, 3 errors ago | InputRegister | 124 | Int | IntegerValue | I219 | 942 | 0 | 100 |  | R
2 | Error History Log, 4 errors ago | InputRegister | 125 | Int | IntegerValue | I220 | 943 | 0 | 100 |  | R
2 | Error History Log, 5 errors ago | InputRegister | 126 | Int | IntegerValue | I221 | 944 | 0 | 100 |  | R
2 | Outdoor Unit 1 Model | InputRegister | 127 | Int | IntegerValue | I222 | 945 | 0 | 32767 |  | R
2 | Outdoor Unit 1 Software version | InputRegister | 128 | Int | IntegerValue | I223 | 946 | 0 | 32767 |  | R
2 | Compressor 1 Type | InputRegister | 129 | Int | IntegerValue | I224 | 947 | 0 | 100 |  | R
2 | Compressor 1 Suction Pressure | InputRegister | 130 | Int | IntegerValue | I225 | 948 | 0 | 6000 | KiloPascals | R
2 | Compressor 1 Discharge Pressure | InputRegister | 131 | Int | IntegerValue | I226 | 949 | 0 | 6000 | KiloPascals | R
2 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 132 | Int | IntegerValue | I227 | 950 | 0 | 3 |  | R
2 | Indoor Coil 1 Fan 1 Speed | InputRegister | 133 | Int | IntegerValue | I228 | 951 | 0 | 9999 | RevolutionsPerMinute | R
2 | Generic Integer 1 | HoldingRegister | 122 | Int | IntegerValue | I229 | 583 |  |  |  | R/W
2 | Generic Integer 2 | HoldingRegister | 123 | Int | IntegerValue | I230 | 584 |  |  |  | R/W
2 | Generic Integer 3 | HoldingRegister | 124 | Int | IntegerValue | I231 | 585 |  |  |  | R/W
2 | Generic Integer 4 | HoldingRegister | 125 | Int | IntegerValue | I232 | 586 |  |  |  | R/W
2 | Generic Integer 5 | HoldingRegister | 126 | Int | IntegerValue | I233 | 587 |  |  |  | R/W
3 | Set Master Setpoint Temperature | HoldingRegister | 140 | Real | AnalogValue | A301 | 588 | 16 | 30 | DegreesCelsius | R/W
3 | Economiser Temperature Difference | HoldingRegister | 144 | Real | AnalogValue | A303 | 590 | 0 | 10 | DegreesCelsius | R/W
3 | Economiser Outside Min Temperature | HoldingRegister | 146 | Real | AnalogValue | A304 | 591 | 0 | 22.5 | DegreesCelsius | R/W
3 | Economiser Outside Max Temperature | HoldingRegister | 148 | Real | AnalogValue | A305 | 592 | 0 | 26 | DegreesCelsius | R/W
3 | Economiser Minimum Damper | HoldingRegister | 150 | Real | AnalogValue | A306 | 593 | 0 | 10 | Volts | R/W
3 | Economiser Maximum Damper | HoldingRegister | 152 | Real | AnalogValue | A307 | 594 | 0 | 10 | Volts | R/W
3 | Economiser Outside Max Moisture | HoldingRegister | 154 | Real | AnalogValue | A308 | 595 | 0 | 100 | GramsPerKilogram | R/W
3 | Economiser Outside Max Dew Point | HoldingRegister | 156 | Real | AnalogValue | A309 | 596 | 0 | 100 | DegreesCelsius | R/W
3 | Economiser Outside Max Enthalpy | HoldingRegister | 158 | Real | AnalogValue | A310 | 597 | 0 | 100 | KilojoulesPerKilogram | R/W
3 | Economiser Enthalpy Delta | HoldingRegister | 160 | Real | AnalogValue | A311 | 598 | 0 | 10 | KilojoulesPerKilogram | R/W
3 | Economiser CO₂ Minimum Damper | HoldingRegister | 162 | Real | AnalogValue | A312 | 599 | 0 | 10 | Volts | R/W
3 | Economiser CO₂ Maximum Damper | HoldingRegister | 164 | Real | AnalogValue | A313 | 600 | 0 | 10 | Volts | R/W
3 | Room Temperature | InputRegister | 142 | Real | AnalogValue | A315 | 953 | -99.9 | 99.9 | DegreesCelsius | R
3 | Indoor Room Temperature | InputRegister | 144 | Real | AnalogValue | A316 | 954 | -99.9 | 99.9 | DegreesCelsius | R
3 | Outside Temperature | InputRegister | 146 | Real | AnalogValue | A317 | 955 | -99.9 | 99.9 | DegreesCelsius | R
3 | Outside Air Temperature | InputRegister | 148 | Real | AnalogValue | A318 | 956 | -99.9 | 99.9 | DegreesCelsius | R
3 | Compressor 1 Suction Temperature | InputRegister | 150 | Real | AnalogValue | A319 | 957 | -999.9 | 999.9 | DegreesCelsius | R
3 | Compressor 1 Discharge Temperature | InputRegister | 152 | Real | AnalogValue | A320 | 958 | -999.9 | 999.9 | DegreesCelsius | R
3 | Compressor 1 Suction SuperHeat | InputRegister | 154 | Real | AnalogValue | A321 | 959 | -99.9 | 99.9 | DegreesCelsius | R
3 | Compressor 1 Suction SuperHeat Target | InputRegister | 156 | Real | AnalogValue | A322 | 960 | -99.9 | 99.9 | DegreesCelsius | R
3 | Outdoor Coil 1 Temperature | InputRegister | 158 | Real | AnalogValue | A323 | 961 | -99.9 | 99.9 | DegreesCelsius | R
3 | Indoor Coil 1 Temperature | InputRegister | 160 | Real | AnalogValue | A324 | 962 | -99.9 | 99.9 | DegreesCelsius | R
3 | Wall Control 1 Temperature | InputRegister | 162 | Real | AnalogValue | A325 | 963 | -99.9 | 99.9 | DegreesCelsius | R
3 | Wall Control 2 Temperature | InputRegister | 164 | Real | AnalogValue | A326 | 964 | -99.9 | 99.9 | DegreesCelsius | R
3 | Wall Control 3 Temperature | InputRegister | 166 | Real | AnalogValue | A327 | 965 | -99.9 | 99.9 | DegreesCelsius | R
3 | Auxillary Sensor 1 Temperature | InputRegister | 168 | Real | AnalogValue | A328 | 966 | -99.9 | 99.9 | DegreesCelsius | R
3 | Auxillary Sensor 2 Temperature | InputRegister | 170 | Real | AnalogValue | A329 | 967 | -99.9 | 99.9 | DegreesCelsius | R
3 | Auxillary Sensor 3 Temperature | InputRegister | 172 | Real | AnalogValue | A330 | 968 | -99.9 | 99.9 | DegreesCelsius | R
3 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 166 | Real | AnalogValue | A331 | 601 | 0 | 100 | Percent | R/W
3 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 168 | Real | AnalogValue | A332 | 602 | 0 | 100 | Percent | R/W
3 | Reduced Airflow Speed | HoldingRegister | 170 | Real | AnalogValue | A333 | 603 | 0 | 100 | Percent | R/W
3 | Economiser Outside Max Humidity | HoldingRegister | 172 | Real | AnalogValue | A334 | 604 | 0 | 100 | Percent | R/W
3 | Actual System Running Capacity | InputRegister | 174 | Real | AnalogValue | A335 | 969 | 0 | 100 | Percent | R
3 | Compressor 1 Demand | InputRegister | 176 | Real | AnalogValue | A336 | 970 | 0 | 100 | Percent | R
3 | Compressor 1 Speed | InputRegister | 178 | Real | AnalogValue | A337 | 971 | 0 | 100 | Percent | R
3 | Indoor Coil 1 Fan Speed | InputRegister | 180 | Real | AnalogValue | A338 | 972 | 0 | 100 | Percent | R
3 | Compressor 1 EEV position | InputRegister | 182 | Real | AnalogValue | A339 | 973 | 0 | 100 | Percent | R
3 | Generic Analog 01 | HoldingRegister | 174 | Real | AnalogValue | A340 | 605 |  |  |  | R/W
3 | Generic Analog 02 | HoldingRegister | 176 | Real | AnalogValue | A341 | 606 |  |  |  | R/W
3 | Generic Analog 03 | HoldingRegister | 178 | Real | AnalogValue | A342 | 607 |  |  |  | R/W
3 | Generic Analog 04 | HoldingRegister | 180 | Real | AnalogValue | A343 | 608 |  |  |  | R/W
3 | Generic Analog 05 | HoldingRegister | 182 | Real | AnalogValue | A344 | 609 |  |  |  | R/W
3 | Turns the AC Off/On (0=Off, 1=On) | Coil | 60 | Bool | BinaryValue | D301 | 55 |  |  |  | R/W
3 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 61 | Bool | BinaryValue | D302 | 56 |  |  |  | R/W
3 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 62 | Bool | BinaryValue | D303 | 57 |  |  |  | R/W
3 | Set Turbo Mode (0=Off, 1=On) | Coil | 63 | Bool | BinaryValue | D304 | 58 |  |  |  | R/W
3 | Set Quiet Mode (0=Off, 1=On) | Coil | 64 | Bool | BinaryValue | D305 | 59 |  |  |  | R/W
3 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 65 | Bool | BinaryValue | D306 | 60 |  |  |  | R/W
3 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 68 | Bool | BinaryValue | D309 | 63 |  |  |  | R/W
3 | Enable Economiser (0=Off, 1=On) | Coil | 69 | Bool | BinaryValue | D310 | 64 |  |  |  | R/W
3 | Enable Humidity Control | Coil | 70 | Bool | BinaryValue | D311 | 65 |  |  |  | R/W
3 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 71 | Bool | BinaryValue | D312 | 66 |  |  |  | R/W
3 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 72 | Bool | BinaryValue | D313 | 67 |  |  |  | R/W
3 | Enable CO₂ Control (0=Off, 1=On) | Coil | 73 | Bool | BinaryValue | D314 | 68 |  |  |  | R/W
3 | Alarm Output (0=Off, 1=On) | DiscreteInput | 60 | Bool | BinaryValue | D315 | 322 |  |  |  | R
3 | Air Filter Notification | DiscreteInput | 61 | Bool | BinaryValue | D316 | 323 |  |  |  | R
3 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 64 | Bool | BinaryValue | D319 | 326 |  |  |  | R
3 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 65 | Bool | BinaryValue | D320 | 327 |  |  |  | R
3 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 66 | Bool | BinaryValue | D321 | 328 |  |  |  | R
3 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 67 | Bool | BinaryValue | D322 | 329 |  |  |  | R
3 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 68 | Bool | BinaryValue | D323 | 330 |  |  |  | R
3 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 69 | Bool | BinaryValue | D324 | 331 |  |  |  | R
3 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 70 | Bool | BinaryValue | D325 | 332 |  |  |  | R
3 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 71 | Bool | BinaryValue | D326 | 333 |  |  |  | R
3 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 72 | Bool | BinaryValue | D327 | 334 |  |  |  | R
3 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 73 | Bool | BinaryValue | D328 | 335 |  |  |  | R
3 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 74 | Bool | BinaryValue | D329 | 336 |  |  |  | R
3 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 75 | Bool | BinaryValue | D330 | 337 |  |  |  | R
3 | Compressor 1 Discharge Temp High | DiscreteInput | 76 | Bool | BinaryValue | D331 | 338 |  |  |  | R
3 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 77 | Bool | BinaryValue | D332 | 339 |  |  |  | R
3 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 78 | Bool | BinaryValue | D333 | 340 |  |  |  | R
3 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 79 | Bool | BinaryValue | D334 | 341 |  |  |  | R
3 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 80 | Bool | BinaryValue | D335 | 342 |  |  |  | R
3 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 81 | Bool | BinaryValue | D336 | 343 |  |  |  | R
3 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 82 | Bool | BinaryValue | D337 | 344 |  |  |  | R
3 | Set zone 1 (0=Off, 1=On) | Coil | 74 | Bool | BinaryValue | D338 | 69 |  |  |  | R/W
3 | Set zone 2 (0=Off, 1=On) | Coil | 75 | Bool | BinaryValue | D339 | 70 |  |  |  | R/W
3 | Set zone 3 (0=Off, 1=On) | Coil | 76 | Bool | BinaryValue | D340 | 71 |  |  |  | R/W
3 | Set zone 4 (0=Off, 1=On) | Coil | 77 | Bool | BinaryValue | D341 | 72 |  |  |  | R/W
3 | Set zone 5 (0=Off, 1=On) | Coil | 78 | Bool | BinaryValue | D342 | 73 |  |  |  | R/W
3 | Set zone 6 (0=Off, 1=On) | Coil | 79 | Bool | BinaryValue | D343 | 74 |  |  |  | R/W
3 | Set zone 7 (0=Off, 1=On) | Coil | 80 | Bool | BinaryValue | D344 | 75 |  |  |  | R/W
3 | Set zone 8 (0=Off, 1=On) | Coil | 81 | Bool | BinaryValue | D345 | 76 |  |  |  | R/W
3 | Generic Digital 1 | Coil | 82 | Bool | BinaryValue | D346 | 77 |  |  |  | R/W
3 | Generic Digital 2 | Coil | 83 | Bool | BinaryValue | D347 | 78 |  |  |  | R/W
3 | Generic Digital 3 | Coil | 84 | Bool | BinaryValue | D348 | 79 |  |  |  | R/W
3 | Generic Digital 4 | Coil | 85 | Bool | BinaryValue | D349 | 80 |  |  |  | R/W
3 | Generic Digital 5 | Coil | 86 | Bool | BinaryValue | D350 | 81 |  |  |  | R/W
3 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 184 | Int | IntegerValue | I301 | 610 | 1 | 4 |  | R/W
3 | Set Air Filter Notification Timer | HoldingRegister | 185 | Int | IntegerValue | I302 | 611 | 1 | 10000 | Hours | R/W
3 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 186 | Int | IntegerValue | I303 | 612 | 1 | 4 |  | R/W
3 | Target Airflow | HoldingRegister | 187 | Int | IntegerValue | I304 | 613 | 0 | 6000 | LitersPerSecond | R/W
3 | Enable Volumetric Airflow | HoldingRegister | 188 | Int | IntegerValue | I305 | 614 | 0 | 6000 | LitersPerSecond | R/W
3 | Indoor Pressure Filter level warning | HoldingRegister | 189 | Int | IntegerValue | I306 | 615 | 0 | 6000 | Pascals | R/W
3 | Economiser CO₂ Low Level | HoldingRegister | 190 | Int | IntegerValue | I307 | 616 | 0 | 1000 | PartsPerMillion | R/W
3 | Economiser CO₂ High Level | HoldingRegister | 191 | Int | IntegerValue | I308 | 617 | 0 | 1000 | PartsPerMillion | R/W
3 | BMS card Software version | InputRegister | 184 | Int | IntegerValue | I309 | 974 | 0 | 32767 |  | R
3 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 185 | Int | IntegerValue | I310 | 975 | 0 | 2 |  | R
3 | Air Filter Run Timer | InputRegister | 186 | Int | IntegerValue | I311 | 976 | 0 | 10000 | Hours | R
3 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 187 | Int | IntegerValue | I312 | 977 | 0 | 4 |  | R
3 | Indoor Airflow | InputRegister | 188 | Int | IntegerValue | I313 | 978 | 0 | 6000 | LitersPerSecond | R
3 | Indoor Static Pressure | InputRegister | 189 | Int | IntegerValue | I314 | 979 | 0 | 6000 | Pascals | R
3 | Measured CO₂ level | InputRegister | 190 | Int | IntegerValue | I315 | 980 | 0 | 1000 | PartsPerMillion | R
3 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 191 | Int | IntegerValue | I316 | 981 | 0 | 100 |  | R
3 | Error History Log, 1 error ago | InputRegister | 192 | Int | IntegerValue | I317 | 982 | 0 | 100 |  | R
3 | Error History Log, 2 errors ago | InputRegister | 193 | Int | IntegerValue | I318 | 983 | 0 | 100 |  | R
3 | Error History Log, 3 errors ago | InputRegister | 194 | Int | IntegerValue | I319 | 984 | 0 | 100 |  | R
3 | Error History Log, 4 errors ago | InputRegister | 195 | Int | IntegerValue | I320 | 985 | 0 | 100 |  | R
3 | Error History Log, 5 errors ago | InputRegister | 196 | Int | IntegerValue | I321 | 986 | 0 | 100 |  | R
3 | Outdoor Unit 1 Model | InputRegister | 197 | Int | IntegerValue | I322 | 987 | 0 | 32767 |  | R
3 | Outdoor Unit 1 Software version | InputRegister | 198 | Int | IntegerValue | I323 | 988 | 0 | 32767 |  | R
3 | Compressor 1 Type | InputRegister | 199 | Int | IntegerValue | I324 | 989 | 0 | 100 |  | R
3 | Compressor 1 Suction Pressure | InputRegister | 200 | Int | IntegerValue | I325 | 990 | 0 | 6000 | KiloPascals | R
3 | Compressor 1 Discharge Pressure | InputRegister | 201 | Int | IntegerValue | I326 | 991 | 0 | 6000 | KiloPascals | R
3 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 202 | Int | IntegerValue | I327 | 992 | 0 | 3 |  | R
3 | Indoor Coil 1 Fan 1 Speed | InputRegister | 203 | Int | IntegerValue | I328 | 993 | 0 | 9999 | RevolutionsPerMinute | R
3 | Generic Integer 1 | HoldingRegister | 192 | Int | IntegerValue | I329 | 618 |  |  |  | R/W
3 | Generic Integer 2 | HoldingRegister | 193 | Int | IntegerValue | I330 | 619 |  |  |  | R/W
3 | Generic Integer 3 | HoldingRegister | 194 | Int | IntegerValue | I331 | 620 |  |  |  | R/W
3 | Generic Integer 4 | HoldingRegister | 195 | Int | IntegerValue | I332 | 621 |  |  |  | R/W
3 | Generic Integer 5 | HoldingRegister | 196 | Int | IntegerValue | I333 | 622 |  |  |  | R/W
4 | Set Master Setpoint Temperature | HoldingRegister | 210 | Real | AnalogValue | A401 | 623 | 16 | 30 | DegreesCelsius | R/W
4 | Economiser Temperature Difference | HoldingRegister | 214 | Real | AnalogValue | A403 | 625 | 0 | 10 | DegreesCelsius | R/W
4 | Economiser Outside Min Temperature | HoldingRegister | 216 | Real | AnalogValue | A404 | 626 | 0 | 22.5 | DegreesCelsius | R/W
4 | Economiser Outside Max Temperature | HoldingRegister | 218 | Real | AnalogValue | A405 | 627 | 0 | 26 | DegreesCelsius | R/W
4 | Economiser Minimum Damper | HoldingRegister | 220 | Real | AnalogValue | A406 | 628 | 0 | 10 | Volts | R/W
4 | Economiser Maximum Damper | HoldingRegister | 222 | Real | AnalogValue | A407 | 629 | 0 | 10 | Volts | R/W
4 | Economiser Outside Max Moisture | HoldingRegister | 224 | Real | AnalogValue | A408 | 630 | 0 | 100 | GramsPerKilogram | R/W
4 | Economiser Outside Max Dew Point | HoldingRegister | 226 | Real | AnalogValue | A409 | 631 | 0 | 100 | DegreesCelsius | R/W
4 | Economiser Outside Max Enthalpy | HoldingRegister | 228 | Real | AnalogValue | A410 | 632 | 0 | 100 | KilojoulesPerKilogram | R/W
4 | Economiser Enthalpy Delta | HoldingRegister | 230 | Real | AnalogValue | A411 | 633 | 0 | 10 | KilojoulesPerKilogram | R/W
4 | Economiser CO₂ Minimum Damper | HoldingRegister | 232 | Real | AnalogValue | A412 | 634 | 0 | 10 | Volts | R/W
4 | Economiser CO₂ Maximum Damper | HoldingRegister | 234 | Real | AnalogValue | A413 | 635 | 0 | 10 | Volts | R/W
4 | Room Temperature | InputRegister | 212 | Real | AnalogValue | A415 | 995 | -99.9 | 99.9 | DegreesCelsius | R
4 | Indoor Room Temperature | InputRegister | 214 | Real | AnalogValue | A416 | 996 | -99.9 | 99.9 | DegreesCelsius | R
4 | Outside Temperature | InputRegister | 216 | Real | AnalogValue | A417 | 997 | -99.9 | 99.9 | DegreesCelsius | R
4 | Outside Air Temperature | InputRegister | 218 | Real | AnalogValue | A418 | 998 | -99.9 | 99.9 | DegreesCelsius | R
4 | Compressor 1 Suction Temperature | InputRegister | 220 | Real | AnalogValue | A419 | 999 | -999.9 | 999.9 | DegreesCelsius | R
4 | Compressor 1 Discharge Temperature | InputRegister | 222 | Real | AnalogValue | A420 | 1000 | -999.9 | 999.9 | DegreesCelsius | R
4 | Compressor 1 Suction SuperHeat | InputRegister | 224 | Real | AnalogValue | A421 | 1001 | -99.9 | 99.9 | DegreesCelsius | R
4 | Compressor 1 Suction SuperHeat Target | InputRegister | 226 | Real | AnalogValue | A422 | 1002 | -99.9 | 99.9 | DegreesCelsius | R
4 | Outdoor Coil 1 Temperature | InputRegister | 228 | Real | AnalogValue | A423 | 1003 | -99.9 | 99.9 | DegreesCelsius | R
4 | Indoor Coil 1 Temperature | InputRegister | 230 | Real | AnalogValue | A424 | 1004 | -99.9 | 99.9 | DegreesCelsius | R
4 | Wall Control 1 Temperature | InputRegister | 232 | Real | AnalogValue | A425 | 1005 | -99.9 | 99.9 | DegreesCelsius | R
4 | Wall Control 2 Temperature | InputRegister | 234 | Real | AnalogValue | A426 | 1006 | -99.9 | 99.9 | DegreesCelsius | R
4 | Wall Control 3 Temperature | InputRegister | 236 | Real | AnalogValue | A427 | 1007 | -99.9 | 99.9 | DegreesCelsius | R
4 | Auxillary Sensor 1 Temperature | InputRegister | 238 | Real | AnalogValue | A428 | 1008 | -99.9 | 99.9 | DegreesCelsius | R
4 | Auxillary Sensor 2 Temperature | InputRegister | 240 | Real | AnalogValue | A429 | 1009 | -99.9 | 99.9 | DegreesCelsius | R
4 | Auxillary Sensor 3 Temperature | InputRegister | 242 | Real | AnalogValue | A430 | 1010 | -99.9 | 99.9 | DegreesCelsius | R
4 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 236 | Real | AnalogValue | A431 | 636 | 0 | 100 | Percent | R/W
4 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 238 | Real | AnalogValue | A432 | 637 | 0 | 100 | Percent | R/W
4 | Reduced Airflow Speed | HoldingRegister | 240 | Real | AnalogValue | A433 | 638 | 0 | 100 | Percent | R/W
4 | Economiser Outside Max Humidity | HoldingRegister | 242 | Real | AnalogValue | A434 | 639 | 0 | 100 | Percent | R/W
4 | Actual System Running Capacity | InputRegister | 244 | Real | AnalogValue | A435 | 1011 | 0 | 100 | Percent | R
4 | Compressor 1 Demand | InputRegister | 246 | Real | AnalogValue | A436 | 1012 | 0 | 100 | Percent | R
4 | Compressor 1 Speed | InputRegister | 248 | Real | AnalogValue | A437 | 1013 | 0 | 100 | Percent | R
4 | Indoor Coil 1 Fan Speed | InputRegister | 250 | Real | AnalogValue | A438 | 1014 | 0 | 100 | Percent | R
4 | Compressor 1 EEV position | InputRegister | 252 | Real | AnalogValue | A439 | 1015 | 0 | 100 | Percent | R
4 | Generic Analog 01 | HoldingRegister | 244 | Real | AnalogValue | A440 | 640 |  |  |  | R/W
4 | Generic Analog 02 | HoldingRegister | 246 | Real | AnalogValue | A441 | 641 |  |  |  | R/W
4 | Generic Analog 03 | HoldingRegister | 248 | Real | AnalogValue | A442 | 642 |  |  |  | R/W
4 | Generic Analog 04 | HoldingRegister | 250 | Real | AnalogValue | A443 | 643 |  |  |  | R/W
4 | Generic Analog 05 | HoldingRegister | 252 | Real | AnalogValue | A444 | 644 |  |  |  | R/W
4 | Turns the AC Off/On (0=Off, 1=On) | Coil | 90 | Bool | BinaryValue | D401 | 82 |  |  |  | R/W
4 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 91 | Bool | BinaryValue | D402 | 83 |  |  |  | R/W
4 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 92 | Bool | BinaryValue | D403 | 84 |  |  |  | R/W
4 | Set Turbo Mode (0=Off, 1=On) | Coil | 93 | Bool | BinaryValue | D404 | 85 |  |  |  | R/W
4 | Set Quiet Mode (0=Off, 1=On) | Coil | 94 | Bool | BinaryValue | D405 | 86 |  |  |  | R/W
4 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 95 | Bool | BinaryValue | D406 | 87 |  |  |  | R/W
4 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 98 | Bool | BinaryValue | D409 | 90 |  |  |  | R/W
4 | Enable Economiser (0=Off, 1=On) | Coil | 99 | Bool | BinaryValue | D410 | 91 |  |  |  | R/W
4 | Enable Humidity Control | Coil | 100 | Bool | BinaryValue | D411 | 92 |  |  |  | R/W
4 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 101 | Bool | BinaryValue | D412 | 93 |  |  |  | R/W
4 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 102 | Bool | BinaryValue | D413 | 94 |  |  |  | R/W
4 | Enable CO₂ Control (0=Off, 1=On) | Coil | 103 | Bool | BinaryValue | D414 | 95 |  |  |  | R/W
4 | Alarm Output (0=Off, 1=On) | DiscreteInput | 90 | Bool | BinaryValue | D415 | 345 |  |  |  | R
4 | Air Filter Notification | DiscreteInput | 91 | Bool | BinaryValue | D416 | 346 |  |  |  | R
4 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 94 | Bool | BinaryValue | D419 | 349 |  |  |  | R
4 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 95 | Bool | BinaryValue | D420 | 350 |  |  |  | R
4 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 96 | Bool | BinaryValue | D421 | 351 |  |  |  | R
4 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 97 | Bool | BinaryValue | D422 | 352 |  |  |  | R
4 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 98 | Bool | BinaryValue | D423 | 353 |  |  |  | R
4 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 99 | Bool | BinaryValue | D424 | 354 |  |  |  | R
4 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 100 | Bool | BinaryValue | D425 | 355 |  |  |  | R
4 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 101 | Bool | BinaryValue | D426 | 356 |  |  |  | R
4 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 102 | Bool | BinaryValue | D427 | 357 |  |  |  | R
4 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 103 | Bool | BinaryValue | D428 | 358 |  |  |  | R
4 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 104 | Bool | BinaryValue | D429 | 359 |  |  |  | R
4 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 105 | Bool | BinaryValue | D430 | 360 |  |  |  | R
4 | Compressor 1 Discharge Temp High | DiscreteInput | 106 | Bool | BinaryValue | D431 | 361 |  |  |  | R
4 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 107 | Bool | BinaryValue | D432 | 362 |  |  |  | R
4 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 108 | Bool | BinaryValue | D433 | 363 |  |  |  | R
4 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 109 | Bool | BinaryValue | D434 | 364 |  |  |  | R
4 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 110 | Bool | BinaryValue | D435 | 365 |  |  |  | R
4 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 111 | Bool | BinaryValue | D436 | 366 |  |  |  | R
4 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 112 | Bool | BinaryValue | D437 | 367 |  |  |  | R
4 | Set zone 1 (0=Off, 1=On) | Coil | 104 | Bool | BinaryValue | D438 | 96 |  |  |  | R/W
4 | Set zone 2 (0=Off, 1=On) | Coil | 105 | Bool | BinaryValue | D439 | 97 |  |  |  | R/W
4 | Set zone 3 (0=Off, 1=On) | Coil | 106 | Bool | BinaryValue | D440 | 98 |  |  |  | R/W
4 | Set zone 4 (0=Off, 1=On) | Coil | 107 | Bool | BinaryValue | D441 | 99 |  |  |  | R/W
4 | Set zone 5 (0=Off, 1=On) | Coil | 108 | Bool | BinaryValue | D442 | 100 |  |  |  | R/W
4 | Set zone 6 (0=Off, 1=On) | Coil | 109 | Bool | BinaryValue | D443 | 101 |  |  |  | R/W
4 | Set zone 7 (0=Off, 1=On) | Coil | 110 | Bool | BinaryValue | D444 | 102 |  |  |  | R/W
4 | Set zone 8 (0=Off, 1=On) | Coil | 111 | Bool | BinaryValue | D445 | 103 |  |  |  | R/W
4 | Generic Digital 1 | Coil | 112 | Bool | BinaryValue | D446 | 104 |  |  |  | R/W
4 | Generic Digital 2 | Coil | 113 | Bool | BinaryValue | D447 | 105 |  |  |  | R/W
4 | Generic Digital 3 | Coil | 114 | Bool | BinaryValue | D448 | 106 |  |  |  | R/W
4 | Generic Digital 4 | Coil | 115 | Bool | BinaryValue | D449 | 107 |  |  |  | R/W
4 | Generic Digital 5 | Coil | 116 | Bool | BinaryValue | D450 | 108 |  |  |  | R/W
4 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 254 | Int | IntegerValue | I401 | 645 | 1 | 4 |  | R/W
4 | Set Air Filter Notification Timer | HoldingRegister | 255 | Int | IntegerValue | I402 | 646 | 1 | 10000 | Hours | R/W
4 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 256 | Int | IntegerValue | I403 | 647 | 1 | 4 |  | R/W
4 | Target Airflow | HoldingRegister | 257 | Int | IntegerValue | I404 | 648 | 0 | 6000 | LitersPerSecond | R/W
4 | Enable Volumetric Airflow | HoldingRegister | 258 | Int | IntegerValue | I405 | 649 | 0 | 6000 | LitersPerSecond | R/W
4 | Indoor Pressure Filter level warning | HoldingRegister | 259 | Int | IntegerValue | I406 | 650 | 0 | 6000 | Pascals | R/W
4 | Economiser CO₂ Low Level | HoldingRegister | 260 | Int | IntegerValue | I407 | 651 | 0 | 1000 | PartsPerMillion | R/W
4 | Economiser CO₂ High Level | HoldingRegister | 261 | Int | IntegerValue | I408 | 652 | 0 | 1000 | PartsPerMillion | R/W
4 | BMS card Software version | InputRegister | 254 | Int | IntegerValue | I409 | 1016 | 0 | 32767 |  | R
4 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 255 | Int | IntegerValue | I410 | 1017 | 0 | 2 |  | R
4 | Air Filter Run Timer | InputRegister | 256 | Int | IntegerValue | I411 | 1018 | 0 | 10000 | Hours | R
4 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 257 | Int | IntegerValue | I412 | 1019 | 0 | 4 |  | R
4 | Indoor Airflow | InputRegister | 258 | Int | IntegerValue | I413 | 1020 | 0 | 6000 | LitersPerSecond | R
4 | Indoor Static Pressure | InputRegister | 259 | Int | IntegerValue | I414 | 1021 | 0 | 6000 | Pascals | R
4 | Measured CO₂ level | InputRegister | 260 | Int | IntegerValue | I415 | 1022 | 0 | 1000 | PartsPerMillion | R
4 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 261 | Int | IntegerValue | I416 | 1023 | 0 | 100 |  | R
4 | Error History Log, 1 error ago | InputRegister | 262 | Int | IntegerValue | I417 | 1024 | 0 | 100 |  | R
4 | Error History Log, 2 errors ago | InputRegister | 263 | Int | IntegerValue | I418 | 1025 | 0 | 100 |  | R
4 | Error History Log, 3 errors ago | InputRegister | 264 | Int | IntegerValue | I419 | 1026 | 0 | 100 |  | R
4 | Error History Log, 4 errors ago | InputRegister | 265 | Int | IntegerValue | I420 | 1027 | 0 | 100 |  | R
4 | Error History Log, 5 errors ago | InputRegister | 266 | Int | IntegerValue | I421 | 1028 | 0 | 100 |  | R
4 | Outdoor Unit 1 Model | InputRegister | 267 | Int | IntegerValue | I422 | 1029 | 0 | 32767 |  | R
4 | Outdoor Unit 1 Software version | InputRegister | 268 | Int | IntegerValue | I423 | 1030 | 0 | 32767 |  | R
4 | Compressor 1 Type | InputRegister | 269 | Int | IntegerValue | I424 | 1031 | 0 | 100 |  | R
4 | Compressor 1 Suction Pressure | InputRegister | 270 | Int | IntegerValue | I425 | 1032 | 0 | 6000 | KiloPascals | R
4 | Compressor 1 Discharge Pressure | InputRegister | 271 | Int | IntegerValue | I426 | 1033 | 0 | 6000 | KiloPascals | R
4 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 272 | Int | IntegerValue | I427 | 1034 | 0 | 3 |  | R
4 | Indoor Coil 1 Fan 1 Speed | InputRegister | 273 | Int | IntegerValue | I428 | 1035 | 0 | 9999 | RevolutionsPerMinute | R
4 | Generic Integer 1 | HoldingRegister | 262 | Int | IntegerValue | I429 | 653 |  |  |  | R/W
4 | Generic Integer 2 | HoldingRegister | 263 | Int | IntegerValue | I430 | 654 |  |  |  | R/W
4 | Generic Integer 3 | HoldingRegister | 264 | Int | IntegerValue | I431 | 655 |  |  |  | R/W
4 | Generic Integer 4 | HoldingRegister | 265 | Int | IntegerValue | I432 | 656 |  |  |  | R/W
4 | Generic Integer 5 | HoldingRegister | 266 | Int | IntegerValue | I433 | 657 |  |  |  | R/W
5 | Set Master Setpoint Temperature | HoldingRegister | 280 | Real | AnalogValue | A501 | 658 | 16 | 30 | DegreesCelsius | R/W
5 | Economiser Temperature Difference | HoldingRegister | 284 | Real | AnalogValue | A503 | 660 | 0 | 10 | DegreesCelsius | R/W
5 | Economiser Outside Min Temperature | HoldingRegister | 286 | Real | AnalogValue | A504 | 661 | 0 | 22.5 | DegreesCelsius | R/W
5 | Economiser Outside Max Temperature | HoldingRegister | 288 | Real | AnalogValue | A505 | 662 | 0 | 26 | DegreesCelsius | R/W
5 | Economiser Minimum Damper | HoldingRegister | 290 | Real | AnalogValue | A506 | 663 | 0 | 10 | Volts | R/W
5 | Economiser Maximum Damper | HoldingRegister | 292 | Real | AnalogValue | A507 | 664 | 0 | 10 | Volts | R/W
5 | Economiser Outside Max Moisture | HoldingRegister | 294 | Real | AnalogValue | A508 | 665 | 0 | 100 | GramsPerKilogram | R/W
5 | Economiser Outside Max Dew Point | HoldingRegister | 296 | Real | AnalogValue | A509 | 666 | 0 | 100 | DegreesCelsius | R/W
5 | Economiser Outside Max Enthalpy | HoldingRegister | 298 | Real | AnalogValue | A510 | 667 | 0 | 100 | KilojoulesPerKilogram | R/W
5 | Economiser Enthalpy Delta | HoldingRegister | 300 | Real | AnalogValue | A511 | 668 | 0 | 10 | KilojoulesPerKilogram | R/W
5 | Economiser CO₂ Minimum Damper | HoldingRegister | 302 | Real | AnalogValue | A512 | 669 | 0 | 10 | Volts | R/W
5 | Economiser CO₂ Maximum Damper | HoldingRegister | 304 | Real | AnalogValue | A513 | 670 | 0 | 10 | Volts | R/W
5 | Room Temperature | InputRegister | 282 | Real | AnalogValue | A515 | 1037 | -99.9 | 99.9 | DegreesCelsius | R
5 | Indoor Room Temperature | InputRegister | 284 | Real | AnalogValue | A516 | 1038 | -99.9 | 99.9 | DegreesCelsius | R
5 | Outside Temperature | InputRegister | 286 | Real | AnalogValue | A517 | 1039 | -99.9 | 99.9 | DegreesCelsius | R
5 | Outside Air Temperature | InputRegister | 288 | Real | AnalogValue | A518 | 1040 | -99.9 | 99.9 | DegreesCelsius | R
5 | Compressor 1 Suction Temperature | InputRegister | 290 | Real | AnalogValue | A519 | 1041 | -999.9 | 999.9 | DegreesCelsius | R
5 | Compressor 1 Discharge Temperature | InputRegister | 292 | Real | AnalogValue | A520 | 1042 | -999.9 | 999.9 | DegreesCelsius | R
5 | Compressor 1 Suction SuperHeat | InputRegister | 294 | Real | AnalogValue | A521 | 1043 | -99.9 | 99.9 | DegreesCelsius | R
5 | Compressor 1 Suction SuperHeat Target | InputRegister | 296 | Real | AnalogValue | A522 | 1044 | -99.9 | 99.9 | DegreesCelsius | R
5 | Outdoor Coil 1 Temperature | InputRegister | 298 | Real | AnalogValue | A523 | 1045 | -99.9 | 99.9 | DegreesCelsius | R
5 | Indoor Coil 1 Temperature | InputRegister | 300 | Real | AnalogValue | A524 | 1046 | -99.9 | 99.9 | DegreesCelsius | R
5 | Wall Control 1 Temperature | InputRegister | 302 | Real | AnalogValue | A525 | 1047 | -99.9 | 99.9 | DegreesCelsius | R
5 | Wall Control 2 Temperature | InputRegister | 304 | Real | AnalogValue | A526 | 1048 | -99.9 | 99.9 | DegreesCelsius | R
5 | Wall Control 3 Temperature | InputRegister | 306 | Real | AnalogValue | A527 | 1049 | -99.9 | 99.9 | DegreesCelsius | R
5 | Auxillary Sensor 1 Temperature | InputRegister | 308 | Real | AnalogValue | A528 | 1050 | -99.9 | 99.9 | DegreesCelsius | R
5 | Auxillary Sensor 2 Temperature | InputRegister | 310 | Real | AnalogValue | A529 | 1051 | -99.9 | 99.9 | DegreesCelsius | R
5 | Auxillary Sensor 3 Temperature | InputRegister | 312 | Real | AnalogValue | A530 | 1052 | -99.9 | 99.9 | DegreesCelsius | R
5 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 306 | Real | AnalogValue | A531 | 671 | 0 | 100 | Percent | R/W
5 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 308 | Real | AnalogValue | A532 | 672 | 0 | 100 | Percent | R/W
5 | Reduced Airflow Speed | HoldingRegister | 310 | Real | AnalogValue | A533 | 673 | 0 | 100 | Percent | R/W
5 | Economiser Outside Max Humidity | HoldingRegister | 312 | Real | AnalogValue | A534 | 674 | 0 | 100 | Percent | R/W
5 | Actual System Running Capacity | InputRegister | 314 | Real | AnalogValue | A535 | 1053 | 0 | 100 | Percent | R
5 | Compressor 1 Demand | InputRegister | 316 | Real | AnalogValue | A536 | 1054 | 0 | 100 | Percent | R
5 | Compressor 1 Speed | InputRegister | 318 | Real | AnalogValue | A537 | 1055 | 0 | 100 | Percent | R
5 | Indoor Coil 1 Fan Speed | InputRegister | 320 | Real | AnalogValue | A538 | 1056 | 0 | 100 | Percent | R
5 | Compressor 1 EEV position | InputRegister | 322 | Real | AnalogValue | A539 | 1057 | 0 | 100 | Percent | R
5 | Generic Analog 01 | HoldingRegister | 314 | Real | AnalogValue | A540 | 675 |  |  |  | R/W
5 | Generic Analog 02 | HoldingRegister | 316 | Real | AnalogValue | A541 | 676 |  |  |  | R/W
5 | Generic Analog 03 | HoldingRegister | 318 | Real | AnalogValue | A542 | 677 |  |  |  | R/W
5 | Generic Analog 04 | HoldingRegister | 320 | Real | AnalogValue | A543 | 678 |  |  |  | R/W
5 | Generic Analog 05 | HoldingRegister | 322 | Real | AnalogValue | A544 | 679 |  |  |  | R/W
5 | Turns the AC Off/On (0=Off, 1=On) | Coil | 120 | Bool | BinaryValue | D501 | 109 |  |  |  | R/W
5 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 121 | Bool | BinaryValue | D502 | 110 |  |  |  | R/W
5 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 122 | Bool | BinaryValue | D503 | 111 |  |  |  | R/W
5 | Set Turbo Mode (0=Off, 1=On) | Coil | 123 | Bool | BinaryValue | D504 | 112 |  |  |  | R/W
5 | Set Quiet Mode (0=Off, 1=On) | Coil | 124 | Bool | BinaryValue | D505 | 113 |  |  |  | R/W
5 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 125 | Bool | BinaryValue | D506 | 114 |  |  |  | R/W
5 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 128 | Bool | BinaryValue | D509 | 117 |  |  |  | R/W
5 | Enable Economiser (0=Off, 1=On) | Coil | 129 | Bool | BinaryValue | D510 | 118 |  |  |  | R/W
5 | Enable Humidity Control | Coil | 130 | Bool | BinaryValue | D511 | 119 |  |  |  | R/W
5 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 131 | Bool | BinaryValue | D512 | 120 |  |  |  | R/W
5 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 132 | Bool | BinaryValue | D513 | 121 |  |  |  | R/W
5 | Enable CO₂ Control (0=Off, 1=On) | Coil | 133 | Bool | BinaryValue | D514 | 122 |  |  |  | R/W
5 | Alarm Output (0=Off, 1=On) | DiscreteInput | 120 | Bool | BinaryValue | D515 | 368 |  |  |  | R
5 | Air Filter Notification | DiscreteInput | 121 | Bool | BinaryValue | D516 | 369 |  |  |  | R
5 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 124 | Bool | BinaryValue | D519 | 372 |  |  |  | R
5 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 125 | Bool | BinaryValue | D520 | 373 |  |  |  | R
5 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 126 | Bool | BinaryValue | D521 | 374 |  |  |  | R
5 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 127 | Bool | BinaryValue | D522 | 375 |  |  |  | R
5 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 128 | Bool | BinaryValue | D523 | 376 |  |  |  | R
5 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 129 | Bool | BinaryValue | D524 | 377 |  |  |  | R
5 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 130 | Bool | BinaryValue | D525 | 378 |  |  |  | R
5 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 131 | Bool | BinaryValue | D526 | 379 |  |  |  | R
5 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 132 | Bool | BinaryValue | D527 | 380 |  |  |  | R
5 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 133 | Bool | BinaryValue | D528 | 381 |  |  |  | R
5 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 134 | Bool | BinaryValue | D529 | 382 |  |  |  | R
5 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 135 | Bool | BinaryValue | D530 | 383 |  |  |  | R
5 | Compressor 1 Discharge Temp High | DiscreteInput | 136 | Bool | BinaryValue | D531 | 384 |  |  |  | R
5 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 137 | Bool | BinaryValue | D532 | 385 |  |  |  | R
5 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 138 | Bool | BinaryValue | D533 | 386 |  |  |  | R
5 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 139 | Bool | BinaryValue | D534 | 387 |  |  |  | R
5 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 140 | Bool | BinaryValue | D535 | 388 |  |  |  | R
5 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 141 | Bool | BinaryValue | D536 | 389 |  |  |  | R
5 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 142 | Bool | BinaryValue | D537 | 390 |  |  |  | R
5 | Set zone 1 (0=Off, 1=On) | Coil | 134 | Bool | BinaryValue | D538 | 123 |  |  |  | R/W
5 | Set zone 2 (0=Off, 1=On) | Coil | 135 | Bool | BinaryValue | D539 | 124 |  |  |  | R/W
5 | Set zone 3 (0=Off, 1=On) | Coil | 136 | Bool | BinaryValue | D540 | 125 |  |  |  | R/W
5 | Set zone 4 (0=Off, 1=On) | Coil | 137 | Bool | BinaryValue | D541 | 126 |  |  |  | R/W
5 | Set zone 5 (0=Off, 1=On) | Coil | 138 | Bool | BinaryValue | D542 | 127 |  |  |  | R/W
5 | Set zone 6 (0=Off, 1=On) | Coil | 139 | Bool | BinaryValue | D543 | 128 |  |  |  | R/W
5 | Set zone 7 (0=Off, 1=On) | Coil | 140 | Bool | BinaryValue | D544 | 129 |  |  |  | R/W
5 | Set zone 8 (0=Off, 1=On) | Coil | 141 | Bool | BinaryValue | D545 | 130 |  |  |  | R/W
5 | Generic Digital 1 | Coil | 142 | Bool | BinaryValue | D546 | 131 |  |  |  | R/W
5 | Generic Digital 2 | Coil | 143 | Bool | BinaryValue | D547 | 132 |  |  |  | R/W
5 | Generic Digital 3 | Coil | 144 | Bool | BinaryValue | D548 | 133 |  |  |  | R/W
5 | Generic Digital 4 | Coil | 145 | Bool | BinaryValue | D549 | 134 |  |  |  | R/W
5 | Generic Digital 5 | Coil | 146 | Bool | BinaryValue | D550 | 135 |  |  |  | R/W
5 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 324 | Int | IntegerValue | I501 | 680 | 1 | 4 |  | R/W
5 | Set Air Filter Notification Timer | HoldingRegister | 325 | Int | IntegerValue | I502 | 681 | 1 | 10000 | Hours | R/W
5 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 326 | Int | IntegerValue | I503 | 682 | 1 | 4 |  | R/W
5 | Target Airflow | HoldingRegister | 327 | Int | IntegerValue | I504 | 683 | 0 | 6000 | LitersPerSecond | R/W
5 | Enable Volumetric Airflow | HoldingRegister | 328 | Int | IntegerValue | I505 | 684 | 0 | 6000 | LitersPerSecond | R/W
5 | Indoor Pressure Filter level warning | HoldingRegister | 329 | Int | IntegerValue | I506 | 685 | 0 | 6000 | Pascals | R/W
5 | Economiser CO₂ Low Level | HoldingRegister | 330 | Int | IntegerValue | I507 | 686 | 0 | 1000 | PartsPerMillion | R/W
5 | Economiser CO₂ High Level | HoldingRegister | 331 | Int | IntegerValue | I508 | 687 | 0 | 1000 | PartsPerMillion | R/W
5 | BMS card Software version | InputRegister | 324 | Int | IntegerValue | I509 | 1058 | 0 | 32767 |  | R
5 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 325 | Int | IntegerValue | I510 | 1059 | 0 | 2 |  | R
5 | Air Filter Run Timer | InputRegister | 326 | Int | IntegerValue | I511 | 1060 | 0 | 10000 | Hours | R
5 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 327 | Int | IntegerValue | I512 | 1061 | 0 | 4 |  | R
5 | Indoor Airflow | InputRegister | 328 | Int | IntegerValue | I513 | 1062 | 0 | 6000 | LitersPerSecond | R
5 | Indoor Static Pressure | InputRegister | 329 | Int | IntegerValue | I514 | 1063 | 0 | 6000 | Pascals | R
5 | Measured CO₂ level | InputRegister | 330 | Int | IntegerValue | I515 | 1064 | 0 | 1000 | PartsPerMillion | R
5 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 331 | Int | IntegerValue | I516 | 1065 | 0 | 100 |  | R
5 | Error History Log, 1 error ago | InputRegister | 332 | Int | IntegerValue | I517 | 1066 | 0 | 100 |  | R
5 | Error History Log, 2 errors ago | InputRegister | 333 | Int | IntegerValue | I518 | 1067 | 0 | 100 |  | R
5 | Error History Log, 3 errors ago | InputRegister | 334 | Int | IntegerValue | I519 | 1068 | 0 | 100 |  | R
5 | Error History Log, 4 errors ago | InputRegister | 335 | Int | IntegerValue | I520 | 1069 | 0 | 100 |  | R
5 | Error History Log, 5 errors ago | InputRegister | 336 | Int | IntegerValue | I521 | 1070 | 0 | 100 |  | R
5 | Outdoor Unit 1 Model | InputRegister | 337 | Int | IntegerValue | I522 | 1071 | 0 | 32767 |  | R
5 | Outdoor Unit 1 Software version | InputRegister | 338 | Int | IntegerValue | I523 | 1072 | 0 | 32767 |  | R
5 | Compressor 1 Type | InputRegister | 339 | Int | IntegerValue | I524 | 1073 | 0 | 100 |  | R
5 | Compressor 1 Suction Pressure | InputRegister | 340 | Int | IntegerValue | I525 | 1074 | 0 | 6000 | KiloPascals | R
5 | Compressor 1 Discharge Pressure | InputRegister | 341 | Int | IntegerValue | I526 | 1075 | 0 | 6000 | KiloPascals | R
5 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 342 | Int | IntegerValue | I527 | 1076 | 0 | 3 |  | R
5 | Indoor Coil 1 Fan 1 Speed | InputRegister | 343 | Int | IntegerValue | I528 | 1077 | 0 | 9999 | RevolutionsPerMinute | R
5 | Generic Integer 1 | HoldingRegister | 332 | Int | IntegerValue | I529 | 688 |  |  |  | R/W
5 | Generic Integer 2 | HoldingRegister | 333 | Int | IntegerValue | I530 | 689 |  |  |  | R/W
5 | Generic Integer 3 | HoldingRegister | 334 | Int | IntegerValue | I531 | 690 |  |  |  | R/W
5 | Generic Integer 4 | HoldingRegister | 335 | Int | IntegerValue | I532 | 691 |  |  |  | R/W
5 | Generic Integer 5 | HoldingRegister | 336 | Int | IntegerValue | I533 | 692 |  |  |  | R/W
6 | Set Master Setpoint Temperature | HoldingRegister | 350 | Real | AnalogValue | A601 | 693 | 16 | 30 | DegreesCelsius | R/W
6 | Economiser Temperature Difference | HoldingRegister | 354 | Real | AnalogValue | A603 | 695 | 0 | 10 | DegreesCelsius | R/W
6 | Economiser Outside Min Temperature | HoldingRegister | 356 | Real | AnalogValue | A604 | 696 | 0 | 22.5 | DegreesCelsius | R/W
6 | Economiser Outside Max Temperature | HoldingRegister | 358 | Real | AnalogValue | A605 | 697 | 0 | 26 | DegreesCelsius | R/W
6 | Economiser Minimum Damper | HoldingRegister | 360 | Real | AnalogValue | A606 | 698 | 0 | 10 | Volts | R/W
6 | Economiser Maximum Damper | HoldingRegister | 362 | Real | AnalogValue | A607 | 699 | 0 | 10 | Volts | R/W
6 | Economiser Outside Max Moisture | HoldingRegister | 364 | Real | AnalogValue | A608 | 700 | 0 | 100 | GramsPerKilogram | R/W
6 | Economiser Outside Max Dew Point | HoldingRegister | 366 | Real | AnalogValue | A609 | 701 | 0 | 100 | DegreesCelsius | R/W
6 | Economiser Outside Max Enthalpy | HoldingRegister | 368 | Real | AnalogValue | A610 | 702 | 0 | 100 | KilojoulesPerKilogram | R/W
6 | Economiser Enthalpy Delta | HoldingRegister | 370 | Real | AnalogValue | A611 | 703 | 0 | 10 | KilojoulesPerKilogram | R/W
6 | Economiser CO₂ Minimum Damper | HoldingRegister | 372 | Real | AnalogValue | A612 | 704 | 0 | 10 | Volts | R/W
6 | Economiser CO₂ Maximum Damper | HoldingRegister | 374 | Real | AnalogValue | A613 | 705 | 0 | 10 | Volts | R/W
6 | Room Temperature | InputRegister | 352 | Real | AnalogValue | A615 | 1079 | -99.9 | 99.9 | DegreesCelsius | R
6 | Indoor Room Temperature | InputRegister | 354 | Real | AnalogValue | A616 | 1080 | -99.9 | 99.9 | DegreesCelsius | R
6 | Outside Temperature | InputRegister | 356 | Real | AnalogValue | A617 | 1081 | -99.9 | 99.9 | DegreesCelsius | R
6 | Outside Air Temperature | InputRegister | 358 | Real | AnalogValue | A618 | 1082 | -99.9 | 99.9 | DegreesCelsius | R
6 | Compressor 1 Suction Temperature | InputRegister | 360 | Real | AnalogValue | A619 | 1083 | -999.9 | 999.9 | DegreesCelsius | R
6 | Compressor 1 Discharge Temperature | InputRegister | 362 | Real | AnalogValue | A620 | 1084 | -999.9 | 999.9 | DegreesCelsius | R
6 | Compressor 1 Suction SuperHeat | InputRegister | 364 | Real | AnalogValue | A621 | 1085 | -99.9 | 99.9 | DegreesCelsius | R
6 | Compressor 1 Suction SuperHeat Target | InputRegister | 366 | Real | AnalogValue | A622 | 1086 | -99.9 | 99.9 | DegreesCelsius | R
6 | Outdoor Coil 1 Temperature | InputRegister | 368 | Real | AnalogValue | A623 | 1087 | -99.9 | 99.9 | DegreesCelsius | R
6 | Indoor Coil 1 Temperature | InputRegister | 370 | Real | AnalogValue | A624 | 1088 | -99.9 | 99.9 | DegreesCelsius | R
6 | Wall Control 1 Temperature | InputRegister | 372 | Real | AnalogValue | A625 | 1089 | -99.9 | 99.9 | DegreesCelsius | R
6 | Wall Control 2 Temperature | InputRegister | 374 | Real | AnalogValue | A626 | 1090 | -99.9 | 99.9 | DegreesCelsius | R
6 | Wall Control 3 Temperature | InputRegister | 376 | Real | AnalogValue | A627 | 1091 | -99.9 | 99.9 | DegreesCelsius | R
6 | Auxillary Sensor 1 Temperature | InputRegister | 378 | Real | AnalogValue | A628 | 1092 | -99.9 | 99.9 | DegreesCelsius | R
6 | Auxillary Sensor 2 Temperature | InputRegister | 380 | Real | AnalogValue | A629 | 1093 | -99.9 | 99.9 | DegreesCelsius | R
6 | Auxillary Sensor 3 Temperature | InputRegister | 382 | Real | AnalogValue | A630 | 1094 | -99.9 | 99.9 | DegreesCelsius | R
6 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 376 | Real | AnalogValue | A631 | 706 | 0 | 100 | Percent | R/W
6 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 378 | Real | AnalogValue | A632 | 707 | 0 | 100 | Percent | R/W
6 | Reduced Airflow Speed | HoldingRegister | 380 | Real | AnalogValue | A633 | 708 | 0 | 100 | Percent | R/W
6 | Economiser Outside Max Humidity | HoldingRegister | 382 | Real | AnalogValue | A634 | 709 | 0 | 100 | Percent | R/W
6 | Actual System Running Capacity | InputRegister | 384 | Real | AnalogValue | A635 | 1095 | 0 | 100 | Percent | R
6 | Compressor 1 Demand | InputRegister | 386 | Real | AnalogValue | A636 | 1096 | 0 | 100 | Percent | R
6 | Compressor 1 Speed | InputRegister | 388 | Real | AnalogValue | A637 | 1097 | 0 | 100 | Percent | R
6 | Indoor Coil 1 Fan Speed | InputRegister | 390 | Real | AnalogValue | A638 | 1098 | 0 | 100 | Percent | R
6 | Compressor 1 EEV position | InputRegister | 392 | Real | AnalogValue | A639 | 1099 | 0 | 100 | Percent | R
6 | Generic Analog 01 | HoldingRegister | 384 | Real | AnalogValue | A640 | 710 |  |  |  | R/W
6 | Generic Analog 02 | HoldingRegister | 386 | Real | AnalogValue | A641 | 711 |  |  |  | R/W
6 | Generic Analog 03 | HoldingRegister | 388 | Real | AnalogValue | A642 | 712 |  |  |  | R/W
6 | Generic Analog 04 | HoldingRegister | 390 | Real | AnalogValue | A643 | 713 |  |  |  | R/W
6 | Generic Analog 05 | HoldingRegister | 392 | Real | AnalogValue | A644 | 714 |  |  |  | R/W
6 | Turns the AC Off/On (0=Off, 1=On) | Coil | 150 | Bool | BinaryValue | D601 | 136 |  |  |  | R/W
6 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 151 | Bool | BinaryValue | D602 | 137 |  |  |  | R/W
6 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 152 | Bool | BinaryValue | D603 | 138 |  |  |  | R/W
6 | Set Turbo Mode (0=Off, 1=On) | Coil | 153 | Bool | BinaryValue | D604 | 139 |  |  |  | R/W
6 | Set Quiet Mode (0=Off, 1=On) | Coil | 154 | Bool | BinaryValue | D605 | 140 |  |  |  | R/W
6 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 155 | Bool | BinaryValue | D606 | 141 |  |  |  | R/W
6 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 158 | Bool | BinaryValue | D609 | 144 |  |  |  | R/W
6 | Enable Economiser (0=Off, 1=On) | Coil | 159 | Bool | BinaryValue | D610 | 145 |  |  |  | R/W
6 | Enable Humidity Control | Coil | 160 | Bool | BinaryValue | D611 | 146 |  |  |  | R/W
6 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 161 | Bool | BinaryValue | D612 | 147 |  |  |  | R/W
6 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 162 | Bool | BinaryValue | D613 | 148 |  |  |  | R/W
6 | Enable CO₂ Control (0=Off, 1=On) | Coil | 163 | Bool | BinaryValue | D614 | 149 |  |  |  | R/W
6 | Alarm Output (0=Off, 1=On) | DiscreteInput | 150 | Bool | BinaryValue | D615 | 391 |  |  |  | R
6 | Air Filter Notification | DiscreteInput | 151 | Bool | BinaryValue | D616 | 392 |  |  |  | R
6 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 154 | Bool | BinaryValue | D619 | 395 |  |  |  | R
6 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 155 | Bool | BinaryValue | D620 | 396 |  |  |  | R
6 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 156 | Bool | BinaryValue | D621 | 397 |  |  |  | R
6 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 157 | Bool | BinaryValue | D622 | 398 |  |  |  | R
6 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 158 | Bool | BinaryValue | D623 | 399 |  |  |  | R
6 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 159 | Bool | BinaryValue | D624 | 400 |  |  |  | R
6 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 160 | Bool | BinaryValue | D625 | 401 |  |  |  | R
6 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 161 | Bool | BinaryValue | D626 | 402 |  |  |  | R
6 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 162 | Bool | BinaryValue | D627 | 403 |  |  |  | R
6 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 163 | Bool | BinaryValue | D628 | 404 |  |  |  | R
6 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 164 | Bool | BinaryValue | D629 | 405 |  |  |  | R
6 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 165 | Bool | BinaryValue | D630 | 406 |  |  |  | R
6 | Compressor 1 Discharge Temp High | DiscreteInput | 166 | Bool | BinaryValue | D631 | 407 |  |  |  | R
6 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 167 | Bool | BinaryValue | D632 | 408 |  |  |  | R
6 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 168 | Bool | BinaryValue | D633 | 409 |  |  |  | R
6 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 169 | Bool | BinaryValue | D634 | 410 |  |  |  | R
6 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 170 | Bool | BinaryValue | D635 | 411 |  |  |  | R
6 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 171 | Bool | BinaryValue | D636 | 412 |  |  |  | R
6 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 172 | Bool | BinaryValue | D637 | 413 |  |  |  | R
6 | Set zone 1 (0=Off, 1=On) | Coil | 164 | Bool | BinaryValue | D638 | 150 |  |  |  | R/W
6 | Set zone 2 (0=Off, 1=On) | Coil | 165 | Bool | BinaryValue | D639 | 151 |  |  |  | R/W
6 | Set zone 3 (0=Off, 1=On) | Coil | 166 | Bool | BinaryValue | D640 | 152 |  |  |  | R/W
6 | Set zone 4 (0=Off, 1=On) | Coil | 167 | Bool | BinaryValue | D641 | 153 |  |  |  | R/W
6 | Set zone 5 (0=Off, 1=On) | Coil | 168 | Bool | BinaryValue | D642 | 154 |  |  |  | R/W
6 | Set zone 6 (0=Off, 1=On) | Coil | 169 | Bool | BinaryValue | D643 | 155 |  |  |  | R/W
6 | Set zone 7 (0=Off, 1=On) | Coil | 170 | Bool | BinaryValue | D644 | 156 |  |  |  | R/W
6 | Set zone 8 (0=Off, 1=On) | Coil | 171 | Bool | BinaryValue | D645 | 157 |  |  |  | R/W
6 | Generic Digital 1 | Coil | 172 | Bool | BinaryValue | D646 | 158 |  |  |  | R/W
6 | Generic Digital 2 | Coil | 173 | Bool | BinaryValue | D647 | 159 |  |  |  | R/W
6 | Generic Digital 3 | Coil | 174 | Bool | BinaryValue | D648 | 160 |  |  |  | R/W
6 | Generic Digital 4 | Coil | 175 | Bool | BinaryValue | D649 | 161 |  |  |  | R/W
6 | Generic Digital 5 | Coil | 176 | Bool | BinaryValue | D650 | 162 |  |  |  | R/W
6 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 394 | Int | IntegerValue | I601 | 715 | 1 | 4 |  | R/W
6 | Set Air Filter Notification Timer | HoldingRegister | 395 | Int | IntegerValue | I602 | 716 | 1 | 10000 | Hours | R/W
6 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 396 | Int | IntegerValue | I603 | 717 | 1 | 4 |  | R/W
6 | Target Airflow | HoldingRegister | 397 | Int | IntegerValue | I604 | 718 | 0 | 6000 | LitersPerSecond | R/W
6 | Enable Volumetric Airflow | HoldingRegister | 398 | Int | IntegerValue | I605 | 719 | 0 | 6000 | LitersPerSecond | R/W
6 | Indoor Pressure Filter level warning | HoldingRegister | 399 | Int | IntegerValue | I606 | 720 | 0 | 6000 | Pascals | R/W
6 | Economiser CO₂ Low Level | HoldingRegister | 400 | Int | IntegerValue | I607 | 721 | 0 | 1000 | PartsPerMillion | R/W
6 | Economiser CO₂ High Level | HoldingRegister | 401 | Int | IntegerValue | I608 | 722 | 0 | 1000 | PartsPerMillion | R/W
6 | BMS card Software version | InputRegister | 394 | Int | IntegerValue | I609 | 1100 | 0 | 32767 |  | R
6 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 395 | Int | IntegerValue | I610 | 1101 | 0 | 2 |  | R
6 | Air Filter Run Timer | InputRegister | 396 | Int | IntegerValue | I611 | 1102 | 0 | 10000 | Hours | R
6 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 397 | Int | IntegerValue | I612 | 1103 | 0 | 4 |  | R
6 | Indoor Airflow | InputRegister | 398 | Int | IntegerValue | I613 | 1104 | 0 | 6000 | LitersPerSecond | R
6 | Indoor Static Pressure | InputRegister | 399 | Int | IntegerValue | I614 | 1105 | 0 | 6000 | Pascals | R
6 | Measured CO₂ level | InputRegister | 400 | Int | IntegerValue | I615 | 1106 | 0 | 1000 | PartsPerMillion | R
6 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 401 | Int | IntegerValue | I616 | 1107 | 0 | 100 |  | R
6 | Error History Log, 1 error ago | InputRegister | 402 | Int | IntegerValue | I617 | 1108 | 0 | 100 |  | R
6 | Error History Log, 2 errors ago | InputRegister | 403 | Int | IntegerValue | I618 | 1109 | 0 | 100 |  | R
6 | Error History Log, 3 errors ago | InputRegister | 404 | Int | IntegerValue | I619 | 1110 | 0 | 100 |  | R
6 | Error History Log, 4 errors ago | InputRegister | 405 | Int | IntegerValue | I620 | 1111 | 0 | 100 |  | R
6 | Error History Log, 5 errors ago | InputRegister | 406 | Int | IntegerValue | I621 | 1112 | 0 | 100 |  | R
6 | Outdoor Unit 1 Model | InputRegister | 407 | Int | IntegerValue | I622 | 1113 | 0 | 32767 |  | R
6 | Outdoor Unit 1 Software version | InputRegister | 408 | Int | IntegerValue | I623 | 1114 | 0 | 32767 |  | R
6 | Compressor 1 Type | InputRegister | 409 | Int | IntegerValue | I624 | 1115 | 0 | 100 |  | R
6 | Compressor 1 Suction Pressure | InputRegister | 410 | Int | IntegerValue | I625 | 1116 | 0 | 6000 | KiloPascals | R
6 | Compressor 1 Discharge Pressure | InputRegister | 411 | Int | IntegerValue | I626 | 1117 | 0 | 6000 | KiloPascals | R
6 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 412 | Int | IntegerValue | I627 | 1118 | 0 | 3 |  | R
6 | Indoor Coil 1 Fan 1 Speed | InputRegister | 413 | Int | IntegerValue | I628 | 1119 | 0 | 9999 | RevolutionsPerMinute | R
6 | Generic Integer 1 | HoldingRegister | 402 | Int | IntegerValue | I629 | 723 |  |  |  | R/W
6 | Generic Integer 2 | HoldingRegister | 403 | Int | IntegerValue | I630 | 724 |  |  |  | R/W
6 | Generic Integer 3 | HoldingRegister | 404 | Int | IntegerValue | I631 | 725 |  |  |  | R/W
6 | Generic Integer 4 | HoldingRegister | 405 | Int | IntegerValue | I632 | 726 |  |  |  | R/W
6 | Generic Integer 5 | HoldingRegister | 406 | Int | IntegerValue | I633 | 727 |  |  |  | R/W
7 | Set Master Setpoint Temperature | HoldingRegister | 420 | Real | AnalogValue | A701 | 728 | 16 | 30 | DegreesCelsius | R/W
7 | Economiser Temperature Difference | HoldingRegister | 424 | Real | AnalogValue | A703 | 730 | 0 | 10 | DegreesCelsius | R/W
7 | Economiser Outside Min Temperature | HoldingRegister | 426 | Real | AnalogValue | A704 | 731 | 0 | 22.5 | DegreesCelsius | R/W
7 | Economiser Outside Max Temperature | HoldingRegister | 428 | Real | AnalogValue | A705 | 732 | 0 | 26 | DegreesCelsius | R/W
7 | Economiser Minimum Damper | HoldingRegister | 430 | Real | AnalogValue | A706 | 733 | 0 | 10 | Volts | R/W
7 | Economiser Maximum Damper | HoldingRegister | 432 | Real | AnalogValue | A707 | 734 | 0 | 10 | Volts | R/W
7 | Economiser Outside Max Moisture | HoldingRegister | 434 | Real | AnalogValue | A708 | 735 | 0 | 100 | GramsPerKilogram | R/W
7 | Economiser Outside Max Dew Point | HoldingRegister | 436 | Real | AnalogValue | A709 | 736 | 0 | 100 | DegreesCelsius | R/W
7 | Economiser Outside Max Enthalpy | HoldingRegister | 438 | Real | AnalogValue | A710 | 737 | 0 | 100 | KilojoulesPerKilogram | R/W
7 | Economiser Enthalpy Delta | HoldingRegister | 440 | Real | AnalogValue | A711 | 738 | 0 | 10 | KilojoulesPerKilogram | R/W
7 | Economiser CO₂ Minimum Damper | HoldingRegister | 442 | Real | AnalogValue | A712 | 739 | 0 | 10 | Volts | R/W
7 | Economiser CO₂ Maximum Damper | HoldingRegister | 444 | Real | AnalogValue | A713 | 740 | 0 | 10 | Volts | R/W
7 | Room Temperature | InputRegister | 422 | Real | AnalogValue | A715 | 1121 | -99.9 | 99.9 | DegreesCelsius | R
7 | Indoor Room Temperature | InputRegister | 424 | Real | AnalogValue | A716 | 1122 | -99.9 | 99.9 | DegreesCelsius | R
7 | Outside Temperature | InputRegister | 426 | Real | AnalogValue | A717 | 1123 | -99.9 | 99.9 | DegreesCelsius | R
7 | Outside Air Temperature | InputRegister | 428 | Real | AnalogValue | A718 | 1124 | -99.9 | 99.9 | DegreesCelsius | R
7 | Compressor 1 Suction Temperature | InputRegister | 430 | Real | AnalogValue | A719 | 1125 | -999.9 | 999.9 | DegreesCelsius | R
7 | Compressor 1 Discharge Temperature | InputRegister | 432 | Real | AnalogValue | A720 | 1126 | -999.9 | 999.9 | DegreesCelsius | R
7 | Compressor 1 Suction SuperHeat | InputRegister | 434 | Real | AnalogValue | A721 | 1127 | -99.9 | 99.9 | DegreesCelsius | R
7 | Compressor 1 Suction SuperHeat Target | InputRegister | 436 | Real | AnalogValue | A722 | 1128 | -99.9 | 99.9 | DegreesCelsius | R
7 | Outdoor Coil 1 Temperature | InputRegister | 438 | Real | AnalogValue | A723 | 1129 | -99.9 | 99.9 | DegreesCelsius | R
7 | Indoor Coil 1 Temperature | InputRegister | 440 | Real | AnalogValue | A724 | 1130 | -99.9 | 99.9 | DegreesCelsius | R
7 | Wall Control 1 Temperature | InputRegister | 442 | Real | AnalogValue | A725 | 1131 | -99.9 | 99.9 | DegreesCelsius | R
7 | Wall Control 2 Temperature | InputRegister | 444 | Real | AnalogValue | A726 | 1132 | -99.9 | 99.9 | DegreesCelsius | R
7 | Wall Control 3 Temperature | InputRegister | 446 | Real | AnalogValue | A727 | 1133 | -99.9 | 99.9 | DegreesCelsius | R
7 | Auxillary Sensor 1 Temperature | InputRegister | 448 | Real | AnalogValue | A728 | 1134 | -99.9 | 99.9 | DegreesCelsius | R
7 | Auxillary Sensor 2 Temperature | InputRegister | 450 | Real | AnalogValue | A729 | 1135 | -99.9 | 99.9 | DegreesCelsius | R
7 | Auxillary Sensor 3 Temperature | InputRegister | 452 | Real | AnalogValue | A730 | 1136 | -99.9 | 99.9 | DegreesCelsius | R
7 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 446 | Real | AnalogValue | A731 | 741 | 0 | 100 | Percent | R/W
7 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 448 | Real | AnalogValue | A732 | 742 | 0 | 100 | Percent | R/W
7 | Reduced Airflow Speed | HoldingRegister | 450 | Real | AnalogValue | A733 | 743 | 0 | 100 | Percent | R/W
7 | Economiser Outside Max Humidity | HoldingRegister | 452 | Real | AnalogValue | A734 | 744 | 0 | 100 | Percent | R/W
7 | Actual System Running Capacity | InputRegister | 454 | Real | AnalogValue | A735 | 1137 | 0 | 100 | Percent | R
7 | Compressor 1 Demand | InputRegister | 456 | Real | AnalogValue | A736 | 1138 | 0 | 100 | Percent | R
7 | Compressor 1 Speed | InputRegister | 458 | Real | AnalogValue | A737 | 1139 | 0 | 100 | Percent | R
7 | Indoor Coil 1 Fan Speed | InputRegister | 460 | Real | AnalogValue | A738 | 1140 | 0 | 100 | Percent | R
7 | Compressor 1 EEV position | InputRegister | 462 | Real | AnalogValue | A739 | 1141 | 0 | 100 | Percent | R
7 | Generic Analog 01 | HoldingRegister | 454 | Real | AnalogValue | A740 | 745 |  |  |  | R/W
7 | Generic Analog 02 | HoldingRegister | 456 | Real | AnalogValue | A741 | 746 |  |  |  | R/W
7 | Generic Analog 03 | HoldingRegister | 458 | Real | AnalogValue | A742 | 747 |  |  |  | R/W
7 | Generic Analog 04 | HoldingRegister | 460 | Real | AnalogValue | A743 | 748 |  |  |  | R/W
7 | Generic Analog 05 | HoldingRegister | 462 | Real | AnalogValue | A744 | 749 |  |  |  | R/W
7 | Turns the AC Off/On (0=Off, 1=On) | Coil | 180 | Bool | BinaryValue | D701 | 163 |  |  |  | R/W
7 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 181 | Bool | BinaryValue | D702 | 164 |  |  |  | R/W
7 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 182 | Bool | BinaryValue | D703 | 165 |  |  |  | R/W
7 | Set Turbo Mode (0=Off, 1=On) | Coil | 183 | Bool | BinaryValue | D704 | 166 |  |  |  | R/W
7 | Set Quiet Mode (0=Off, 1=On) | Coil | 184 | Bool | BinaryValue | D705 | 167 |  |  |  | R/W
7 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 185 | Bool | BinaryValue | D706 | 168 |  |  |  | R/W
7 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 188 | Bool | BinaryValue | D709 | 171 |  |  |  | R/W
7 | Enable Economiser (0=Off, 1=On) | Coil | 189 | Bool | BinaryValue | D710 | 172 |  |  |  | R/W
7 | Enable Humidity Control | Coil | 190 | Bool | BinaryValue | D711 | 173 |  |  |  | R/W
7 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 191 | Bool | BinaryValue | D712 | 174 |  |  |  | R/W
7 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 192 | Bool | BinaryValue | D713 | 175 |  |  |  | R/W
7 | Enable CO₂ Control (0=Off, 1=On) | Coil | 193 | Bool | BinaryValue | D714 | 176 |  |  |  | R/W
7 | Alarm Output (0=Off, 1=On) | DiscreteInput | 180 | Bool | BinaryValue | D715 | 414 |  |  |  | R
7 | Air Filter Notification | DiscreteInput | 181 | Bool | BinaryValue | D716 | 415 |  |  |  | R
7 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 184 | Bool | BinaryValue | D719 | 418 |  |  |  | R
7 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 185 | Bool | BinaryValue | D720 | 419 |  |  |  | R
7 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 186 | Bool | BinaryValue | D721 | 420 |  |  |  | R
7 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 187 | Bool | BinaryValue | D722 | 421 |  |  |  | R
7 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 188 | Bool | BinaryValue | D723 | 422 |  |  |  | R
7 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 189 | Bool | BinaryValue | D724 | 423 |  |  |  | R
7 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 190 | Bool | BinaryValue | D725 | 424 |  |  |  | R
7 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 191 | Bool | BinaryValue | D726 | 425 |  |  |  | R
7 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 192 | Bool | BinaryValue | D727 | 426 |  |  |  | R
7 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 193 | Bool | BinaryValue | D728 | 427 |  |  |  | R
7 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 194 | Bool | BinaryValue | D729 | 428 |  |  |  | R
7 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 195 | Bool | BinaryValue | D730 | 429 |  |  |  | R
7 | Compressor 1 Discharge Temp High | DiscreteInput | 196 | Bool | BinaryValue | D731 | 430 |  |  |  | R
7 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 197 | Bool | BinaryValue | D732 | 431 |  |  |  | R
7 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 198 | Bool | BinaryValue | D733 | 432 |  |  |  | R
7 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 199 | Bool | BinaryValue | D734 | 433 |  |  |  | R
7 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 200 | Bool | BinaryValue | D735 | 434 |  |  |  | R
7 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 201 | Bool | BinaryValue | D736 | 435 |  |  |  | R
7 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 202 | Bool | BinaryValue | D737 | 436 |  |  |  | R
7 | Set zone 1 (0=Off, 1=On) | Coil | 194 | Bool | BinaryValue | D738 | 177 |  |  |  | R/W
7 | Set zone 2 (0=Off, 1=On) | Coil | 195 | Bool | BinaryValue | D739 | 178 |  |  |  | R/W
7 | Set zone 3 (0=Off, 1=On) | Coil | 196 | Bool | BinaryValue | D740 | 179 |  |  |  | R/W
7 | Set zone 4 (0=Off, 1=On) | Coil | 197 | Bool | BinaryValue | D741 | 180 |  |  |  | R/W
7 | Set zone 5 (0=Off, 1=On) | Coil | 198 | Bool | BinaryValue | D742 | 181 |  |  |  | R/W
7 | Set zone 6 (0=Off, 1=On) | Coil | 199 | Bool | BinaryValue | D743 | 182 |  |  |  | R/W
7 | Set zone 7 (0=Off, 1=On) | Coil | 200 | Bool | BinaryValue | D744 | 183 |  |  |  | R/W
7 | Set zone 8 (0=Off, 1=On) | Coil | 201 | Bool | BinaryValue | D745 | 184 |  |  |  | R/W
7 | Generic Digital 1 | Coil | 202 | Bool | BinaryValue | D746 | 185 |  |  |  | R/W
7 | Generic Digital 2 | Coil | 203 | Bool | BinaryValue | D747 | 186 |  |  |  | R/W
7 | Generic Digital 3 | Coil | 204 | Bool | BinaryValue | D748 | 187 |  |  |  | R/W
7 | Generic Digital 4 | Coil | 205 | Bool | BinaryValue | D749 | 188 |  |  |  | R/W
7 | Generic Digital 5 | Coil | 206 | Bool | BinaryValue | D750 | 189 |  |  |  | R/W
7 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 464 | Int | IntegerValue | I701 | 750 | 1 | 4 |  | R/W
7 | Set Air Filter Notification Timer | HoldingRegister | 465 | Int | IntegerValue | I702 | 751 | 1 | 10000 | Hours | R/W
7 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 466 | Int | IntegerValue | I703 | 752 | 1 | 4 |  | R/W
7 | Target Airflow | HoldingRegister | 467 | Int | IntegerValue | I704 | 753 | 0 | 6000 | LitersPerSecond | R/W
7 | Enable Volumetric Airflow | HoldingRegister | 468 | Int | IntegerValue | I705 | 754 | 0 | 6000 | LitersPerSecond | R/W
7 | Indoor Pressure Filter level warning | HoldingRegister | 469 | Int | IntegerValue | I706 | 755 | 0 | 6000 | Pascals | R/W
7 | Economiser CO₂ Low Level | HoldingRegister | 470 | Int | IntegerValue | I707 | 756 | 0 | 1000 | PartsPerMillion | R/W
7 | Economiser CO₂ High Level | HoldingRegister | 471 | Int | IntegerValue | I708 | 757 | 0 | 1000 | PartsPerMillion | R/W
7 | BMS card Software version | InputRegister | 464 | Int | IntegerValue | I709 | 1142 | 0 | 32767 |  | R
7 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 465 | Int | IntegerValue | I710 | 1143 | 0 | 2 |  | R
7 | Air Filter Run Timer | InputRegister | 466 | Int | IntegerValue | I711 | 1144 | 0 | 10000 | Hours | R
7 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 467 | Int | IntegerValue | I712 | 1145 | 0 | 4 |  | R
7 | Indoor Airflow | InputRegister | 468 | Int | IntegerValue | I713 | 1146 | 0 | 6000 | LitersPerSecond | R
7 | Indoor Static Pressure | InputRegister | 469 | Int | IntegerValue | I714 | 1147 | 0 | 6000 | Pascals | R
7 | Measured CO₂ level | InputRegister | 470 | Int | IntegerValue | I715 | 1148 | 0 | 1000 | PartsPerMillion | R
7 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 471 | Int | IntegerValue | I716 | 1149 | 0 | 100 |  | R
7 | Error History Log, 1 error ago | InputRegister | 472 | Int | IntegerValue | I717 | 1150 | 0 | 100 |  | R
7 | Error History Log, 2 errors ago | InputRegister | 473 | Int | IntegerValue | I718 | 1151 | 0 | 100 |  | R
7 | Error History Log, 3 errors ago | InputRegister | 474 | Int | IntegerValue | I719 | 1152 | 0 | 100 |  | R
7 | Error History Log, 4 errors ago | InputRegister | 475 | Int | IntegerValue | I720 | 1153 | 0 | 100 |  | R
7 | Error History Log, 5 errors ago | InputRegister | 476 | Int | IntegerValue | I721 | 1154 | 0 | 100 |  | R
7 | Outdoor Unit 1 Model | InputRegister | 477 | Int | IntegerValue | I722 | 1155 | 0 | 32767 |  | R
7 | Outdoor Unit 1 Software version | InputRegister | 478 | Int | IntegerValue | I723 | 1156 | 0 | 32767 |  | R
7 | Compressor 1 Type | InputRegister | 479 | Int | IntegerValue | I724 | 1157 | 0 | 100 |  | R
7 | Compressor 1 Suction Pressure | InputRegister | 480 | Int | IntegerValue | I725 | 1158 | 0 | 6000 | KiloPascals | R
7 | Compressor 1 Discharge Pressure | InputRegister | 481 | Int | IntegerValue | I726 | 1159 | 0 | 6000 | KiloPascals | R
7 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 482 | Int | IntegerValue | I727 | 1160 | 0 | 3 |  | R
7 | Indoor Coil 1 Fan 1 Speed | InputRegister | 483 | Int | IntegerValue | I728 | 1161 | 0 | 9999 | RevolutionsPerMinute | R
7 | Generic Integer 1 | HoldingRegister | 472 | Int | IntegerValue | I729 | 758 |  |  |  | R/W
7 | Generic Integer 2 | HoldingRegister | 473 | Int | IntegerValue | I730 | 759 |  |  |  | R/W
7 | Generic Integer 3 | HoldingRegister | 474 | Int | IntegerValue | I731 | 760 |  |  |  | R/W
7 | Generic Integer 4 | HoldingRegister | 475 | Int | IntegerValue | I732 | 761 |  |  |  | R/W
7 | Generic Integer 5 | HoldingRegister | 476 | Int | IntegerValue | I733 | 762 |  |  |  | R/W
8 | Set Master Setpoint Temperature | HoldingRegister | 490 | Real | AnalogValue | A801 | 763 | 16 | 30 | DegreesCelsius | R/W
8 | Economiser Temperature Difference | HoldingRegister | 494 | Real | AnalogValue | A803 | 765 | 0 | 10 | DegreesCelsius | R/W
8 | Economiser Outside Min Temperature | HoldingRegister | 496 | Real | AnalogValue | A804 | 766 | 0 | 22.5 | DegreesCelsius | R/W
8 | Economiser Outside Max Temperature | HoldingRegister | 498 | Real | AnalogValue | A805 | 767 | 0 | 26 | DegreesCelsius | R/W
8 | Economiser Minimum Damper | HoldingRegister | 500 | Real | AnalogValue | A806 | 768 | 0 | 10 | Volts | R/W
8 | Economiser Maximum Damper | HoldingRegister | 502 | Real | AnalogValue | A807 | 769 | 0 | 10 | Volts | R/W
8 | Economiser Outside Max Moisture | HoldingRegister | 504 | Real | AnalogValue | A808 | 770 | 0 | 100 | GramsPerKilogram | R/W
8 | Economiser Outside Max Dew Point | HoldingRegister | 506 | Real | AnalogValue | A809 | 771 | 0 | 100 | DegreesCelsius | R/W
8 | Economiser Outside Max Enthalpy | HoldingRegister | 508 | Real | AnalogValue | A810 | 772 | 0 | 100 | KilojoulesPerKilogram | R/W
8 | Economiser Enthalpy Delta | HoldingRegister | 510 | Real | AnalogValue | A811 | 773 | 0 | 10 | KilojoulesPerKilogram | R/W
8 | Economiser CO₂ Minimum Damper | HoldingRegister | 512 | Real | AnalogValue | A812 | 774 | 0 | 10 | Volts | R/W
8 | Economiser CO₂ Maximum Damper | HoldingRegister | 514 | Real | AnalogValue | A813 | 775 | 0 | 10 | Volts | R/W
8 | Room Temperature | InputRegister | 492 | Real | AnalogValue | A815 | 1163 | -99.9 | 99.9 | DegreesCelsius | R
8 | Indoor Room Temperature | InputRegister | 494 | Real | AnalogValue | A816 | 1164 | -99.9 | 99.9 | DegreesCelsius | R
8 | Outside Temperature | InputRegister | 496 | Real | AnalogValue | A817 | 1165 | -99.9 | 99.9 | DegreesCelsius | R
8 | Outside Air Temperature | InputRegister | 498 | Real | AnalogValue | A818 | 1166 | -99.9 | 99.9 | DegreesCelsius | R
8 | Compressor 1 Suction Temperature | InputRegister | 500 | Real | AnalogValue | A819 | 1167 | -999.9 | 999.9 | DegreesCelsius | R
8 | Compressor 1 Discharge Temperature | InputRegister | 502 | Real | AnalogValue | A820 | 1168 | -999.9 | 999.9 | DegreesCelsius | R
8 | Compressor 1 Suction SuperHeat | InputRegister | 504 | Real | AnalogValue | A821 | 1169 | -99.9 | 99.9 | DegreesCelsius | R
8 | Compressor 1 Suction SuperHeat Target | InputRegister | 506 | Real | AnalogValue | A822 | 1170 | -99.9 | 99.9 | DegreesCelsius | R
8 | Outdoor Coil 1 Temperature | InputRegister | 508 | Real | AnalogValue | A823 | 1171 | -99.9 | 99.9 | DegreesCelsius | R
8 | Indoor Coil 1 Temperature | InputRegister | 510 | Real | AnalogValue | A824 | 1172 | -99.9 | 99.9 | DegreesCelsius | R
8 | Wall Control 1 Temperature | InputRegister | 512 | Real | AnalogValue | A825 | 1173 | -99.9 | 99.9 | DegreesCelsius | R
8 | Wall Control 2 Temperature | InputRegister | 514 | Real | AnalogValue | A826 | 1174 | -99.9 | 99.9 | DegreesCelsius | R
8 | Wall Control 3 Temperature | InputRegister | 516 | Real | AnalogValue | A827 | 1175 | -99.9 | 99.9 | DegreesCelsius | R
8 | Auxillary Sensor 1 Temperature | InputRegister | 518 | Real | AnalogValue | A828 | 1176 | -99.9 | 99.9 | DegreesCelsius | R
8 | Auxillary Sensor 2 Temperature | InputRegister | 520 | Real | AnalogValue | A829 | 1177 | -99.9 | 99.9 | DegreesCelsius | R
8 | Auxillary Sensor 3 Temperature | InputRegister | 522 | Real | AnalogValue | A830 | 1178 | -99.9 | 99.9 | DegreesCelsius | R
8 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 516 | Real | AnalogValue | A831 | 776 | 0 | 100 | Percent | R/W
8 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 518 | Real | AnalogValue | A832 | 777 | 0 | 100 | Percent | R/W
8 | Reduced Airflow Speed | HoldingRegister | 520 | Real | AnalogValue | A833 | 778 | 0 | 100 | Percent | R/W
8 | Economiser Outside Max Humidity | HoldingRegister | 522 | Real | AnalogValue | A834 | 779 | 0 | 100 | Percent | R/W
8 | Actual System Running Capacity | InputRegister | 524 | Real | AnalogValue | A835 | 1179 | 0 | 100 | Percent | R
8 | Compressor 1 Demand | InputRegister | 526 | Real | AnalogValue | A836 | 1180 | 0 | 100 | Percent | R
8 | Compressor 1 Speed | InputRegister | 528 | Real | AnalogValue | A837 | 1181 | 0 | 100 | Percent | R
8 | Indoor Coil 1 Fan Speed | InputRegister | 530 | Real | AnalogValue | A838 | 1182 | 0 | 100 | Percent | R
8 | Compressor 1 EEV position | InputRegister | 532 | Real | AnalogValue | A839 | 1183 | 0 | 100 | Percent | R
8 | Generic Analog 01 | HoldingRegister | 524 | Real | AnalogValue | A840 | 780 |  |  |  | R/W
8 | Generic Analog 02 | HoldingRegister | 526 | Real | AnalogValue | A841 | 781 |  |  |  | R/W
8 | Generic Analog 03 | HoldingRegister | 528 | Real | AnalogValue | A842 | 782 |  |  |  | R/W
8 | Generic Analog 04 | HoldingRegister | 530 | Real | AnalogValue | A843 | 783 |  |  |  | R/W
8 | Generic Analog 05 | HoldingRegister | 532 | Real | AnalogValue | A844 | 784 |  |  |  | R/W
8 | Turns the AC Off/On (0=Off, 1=On) | Coil | 210 | Bool | BinaryValue | D801 | 190 |  |  |  | R/W
8 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 211 | Bool | BinaryValue | D802 | 191 |  |  |  | R/W
8 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 212 | Bool | BinaryValue | D803 | 192 |  |  |  | R/W
8 | Set Turbo Mode (0=Off, 1=On) | Coil | 213 | Bool | BinaryValue | D804 | 193 |  |  |  | R/W
8 | Set Quiet Mode (0=Off, 1=On) | Coil | 214 | Bool | BinaryValue | D805 | 194 |  |  |  | R/W
8 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 215 | Bool | BinaryValue | D806 | 195 |  |  |  | R/W
8 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 218 | Bool | BinaryValue | D809 | 198 |  |  |  | R/W
8 | Enable Economiser (0=Off, 1=On) | Coil | 219 | Bool | BinaryValue | D810 | 199 |  |  |  | R/W
8 | Enable Humidity Control | Coil | 220 | Bool | BinaryValue | D811 | 200 |  |  |  | R/W
8 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 221 | Bool | BinaryValue | D812 | 201 |  |  |  | R/W
8 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 222 | Bool | BinaryValue | D813 | 202 |  |  |  | R/W
8 | Enable CO₂ Control (0=Off, 1=On) | Coil | 223 | Bool | BinaryValue | D814 | 203 |  |  |  | R/W
8 | Alarm Output (0=Off, 1=On) | DiscreteInput | 210 | Bool | BinaryValue | D815 | 437 |  |  |  | R
8 | Air Filter Notification | DiscreteInput | 211 | Bool | BinaryValue | D816 | 438 |  |  |  | R
8 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 214 | Bool | BinaryValue | D819 | 441 |  |  |  | R
8 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 215 | Bool | BinaryValue | D820 | 442 |  |  |  | R
8 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 216 | Bool | BinaryValue | D821 | 443 |  |  |  | R
8 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 217 | Bool | BinaryValue | D822 | 444 |  |  |  | R
8 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 218 | Bool | BinaryValue | D823 | 445 |  |  |  | R
8 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 219 | Bool | BinaryValue | D824 | 446 |  |  |  | R
8 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 220 | Bool | BinaryValue | D825 | 447 |  |  |  | R
8 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 221 | Bool | BinaryValue | D826 | 448 |  |  |  | R
8 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 222 | Bool | BinaryValue | D827 | 449 |  |  |  | R
8 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 223 | Bool | BinaryValue | D828 | 450 |  |  |  | R
8 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 224 | Bool | BinaryValue | D829 | 451 |  |  |  | R
8 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 225 | Bool | BinaryValue | D830 | 452 |  |  |  | R
8 | Compressor 1 Discharge Temp High | DiscreteInput | 226 | Bool | BinaryValue | D831 | 453 |  |  |  | R
8 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 227 | Bool | BinaryValue | D832 | 454 |  |  |  | R
8 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 228 | Bool | BinaryValue | D833 | 455 |  |  |  | R
8 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 229 | Bool | BinaryValue | D834 | 456 |  |  |  | R
8 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 230 | Bool | BinaryValue | D835 | 457 |  |  |  | R
8 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 231 | Bool | BinaryValue | D836 | 458 |  |  |  | R
8 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 232 | Bool | BinaryValue | D837 | 459 |  |  |  | R
8 | Set zone 1 (0=Off, 1=On) | Coil | 224 | Bool | BinaryValue | D838 | 204 |  |  |  | R/W
8 | Set zone 2 (0=Off, 1=On) | Coil | 225 | Bool | BinaryValue | D839 | 205 |  |  |  | R/W
8 | Set zone 3 (0=Off, 1=On) | Coil | 226 | Bool | BinaryValue | D840 | 206 |  |  |  | R/W
8 | Set zone 4 (0=Off, 1=On) | Coil | 227 | Bool | BinaryValue | D841 | 207 |  |  |  | R/W
8 | Set zone 5 (0=Off, 1=On) | Coil | 228 | Bool | BinaryValue | D842 | 208 |  |  |  | R/W
8 | Set zone 6 (0=Off, 1=On) | Coil | 229 | Bool | BinaryValue | D843 | 209 |  |  |  | R/W
8 | Set zone 7 (0=Off, 1=On) | Coil | 230 | Bool | BinaryValue | D844 | 210 |  |  |  | R/W
8 | Set zone 8 (0=Off, 1=On) | Coil | 231 | Bool | BinaryValue | D845 | 211 |  |  |  | R/W
8 | Generic Digital 1 | Coil | 232 | Bool | BinaryValue | D846 | 212 |  |  |  | R/W
8 | Generic Digital 2 | Coil | 233 | Bool | BinaryValue | D847 | 213 |  |  |  | R/W
8 | Generic Digital 3 | Coil | 234 | Bool | BinaryValue | D848 | 214 |  |  |  | R/W
8 | Generic Digital 4 | Coil | 235 | Bool | BinaryValue | D849 | 215 |  |  |  | R/W
8 | Generic Digital 5 | Coil | 236 | Bool | BinaryValue | D850 | 216 |  |  |  | R/W
8 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 534 | Int | IntegerValue | I801 | 785 | 1 | 4 |  | R/W
8 | Set Air Filter Notification Timer | HoldingRegister | 535 | Int | IntegerValue | I802 | 786 | 1 | 10000 | Hours | R/W
8 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 536 | Int | IntegerValue | I803 | 787 | 1 | 4 |  | R/W
8 | Target Airflow | HoldingRegister | 537 | Int | IntegerValue | I804 | 788 | 0 | 6000 | LitersPerSecond | R/W
8 | Enable Volumetric Airflow | HoldingRegister | 538 | Int | IntegerValue | I805 | 789 | 0 | 6000 | LitersPerSecond | R/W
8 | Indoor Pressure Filter level warning | HoldingRegister | 539 | Int | IntegerValue | I806 | 790 | 0 | 6000 | Pascals | R/W
8 | Economiser CO₂ Low Level | HoldingRegister | 540 | Int | IntegerValue | I807 | 791 | 0 | 1000 | PartsPerMillion | R/W
8 | Economiser CO₂ High Level | HoldingRegister | 541 | Int | IntegerValue | I808 | 792 | 0 | 1000 | PartsPerMillion | R/W
8 | BMS card Software version | InputRegister | 534 | Int | IntegerValue | I809 | 1184 | 0 | 32767 |  | R
8 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 535 | Int | IntegerValue | I810 | 1185 | 0 | 2 |  | R
8 | Air Filter Run Timer | InputRegister | 536 | Int | IntegerValue | I811 | 1186 | 0 | 10000 | Hours | R
8 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 537 | Int | IntegerValue | I812 | 1187 | 0 | 4 |  | R
8 | Indoor Airflow | InputRegister | 538 | Int | IntegerValue | I813 | 1188 | 0 | 6000 | LitersPerSecond | R
8 | Indoor Static Pressure | InputRegister | 539 | Int | IntegerValue | I814 | 1189 | 0 | 6000 | Pascals | R
8 | Measured CO₂ level | InputRegister | 540 | Int | IntegerValue | I815 | 1190 | 0 | 1000 | PartsPerMillion | R
8 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 541 | Int | IntegerValue | I816 | 1191 | 0 | 100 |  | R
8 | Error History Log, 1 error ago | InputRegister | 542 | Int | IntegerValue | I817 | 1192 | 0 | 100 |  | R
8 | Error History Log, 2 errors ago | InputRegister | 543 | Int | IntegerValue | I818 | 1193 | 0 | 100 |  | R
8 | Error History Log, 3 errors ago | InputRegister | 544 | Int | IntegerValue | I819 | 1194 | 0 | 100 |  | R
8 | Error History Log, 4 errors ago | InputRegister | 545 | Int | IntegerValue | I820 | 1195 | 0 | 100 |  | R
8 | Error History Log, 5 errors ago | InputRegister | 546 | Int | IntegerValue | I821 | 1196 | 0 | 100 |  | R
8 | Outdoor Unit 1 Model | InputRegister | 547 | Int | IntegerValue | I822 | 1197 | 0 | 32767 |  | R
8 | Outdoor Unit 1 Software version | InputRegister | 548 | Int | IntegerValue | I823 | 1198 | 0 | 32767 |  | R
8 | Compressor 1 Type | InputRegister | 549 | Int | IntegerValue | I824 | 1199 | 0 | 100 |  | R
8 | Compressor 1 Suction Pressure | InputRegister | 550 | Int | IntegerValue | I825 | 1200 | 0 | 6000 | KiloPascals | R
8 | Compressor 1 Discharge Pressure | InputRegister | 551 | Int | IntegerValue | I826 | 1201 | 0 | 6000 | KiloPascals | R
8 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 552 | Int | IntegerValue | I827 | 1202 | 0 | 3 |  | R
8 | Indoor Coil 1 Fan 1 Speed | InputRegister | 553 | Int | IntegerValue | I828 | 1203 | 0 | 9999 | RevolutionsPerMinute | R
8 | Generic Integer 1 | HoldingRegister | 542 | Int | IntegerValue | I829 | 793 |  |  |  | R/W
8 | Generic Integer 2 | HoldingRegister | 543 | Int | IntegerValue | I830 | 794 |  |  |  | R/W
8 | Generic Integer 3 | HoldingRegister | 544 | Int | IntegerValue | I831 | 795 |  |  |  | R/W
8 | Generic Integer 4 | HoldingRegister | 545 | Int | IntegerValue | I832 | 796 |  |  |  | R/W
8 | Generic Integer 5 | HoldingRegister | 546 | Int | IntegerValue | I833 | 797 |  |  |  | R/W
9 | Set Master Setpoint Temperature | HoldingRegister | 560 | Real | AnalogValue | A901 | 798 | 16 | 30 | DegreesCelsius | R/W
9 | Economiser Temperature Difference | HoldingRegister | 564 | Real | AnalogValue | A903 | 800 | 0 | 10 | DegreesCelsius | R/W
9 | Economiser Outside Min Temperature | HoldingRegister | 566 | Real | AnalogValue | A904 | 801 | 0 | 22.5 | DegreesCelsius | R/W
9 | Economiser Outside Max Temperature | HoldingRegister | 568 | Real | AnalogValue | A905 | 802 | 0 | 26 | DegreesCelsius | R/W
9 | Economiser Minimum Damper | HoldingRegister | 570 | Real | AnalogValue | A906 | 803 | 0 | 10 | Volts | R/W
9 | Economiser Maximum Damper | HoldingRegister | 572 | Real | AnalogValue | A907 | 804 | 0 | 10 | Volts | R/W
9 | Economiser Outside Max Moisture | HoldingRegister | 574 | Real | AnalogValue | A908 | 805 | 0 | 100 | GramsPerKilogram | R/W
9 | Economiser Outside Max Dew Point | HoldingRegister | 576 | Real | AnalogValue | A909 | 806 | 0 | 100 | DegreesCelsius | R/W
9 | Economiser Outside Max Enthalpy | HoldingRegister | 578 | Real | AnalogValue | A910 | 807 | 0 | 100 | KilojoulesPerKilogram | R/W
9 | Economiser Enthalpy Delta | HoldingRegister | 580 | Real | AnalogValue | A911 | 808 | 0 | 10 | KilojoulesPerKilogram | R/W
9 | Economiser CO₂ Minimum Damper | HoldingRegister | 582 | Real | AnalogValue | A912 | 809 | 0 | 10 | Volts | R/W
9 | Economiser CO₂ Maximum Damper | HoldingRegister | 584 | Real | AnalogValue | A913 | 810 | 0 | 10 | Volts | R/W
9 | Room Temperature | InputRegister | 562 | Real | AnalogValue | A915 | 1205 | -99.9 | 99.9 | DegreesCelsius | R
9 | Indoor Room Temperature | InputRegister | 564 | Real | AnalogValue | A916 | 1206 | -99.9 | 99.9 | DegreesCelsius | R
9 | Outside Temperature | InputRegister | 566 | Real | AnalogValue | A917 | 1207 | -99.9 | 99.9 | DegreesCelsius | R
9 | Outside Air Temperature | InputRegister | 568 | Real | AnalogValue | A918 | 1208 | -99.9 | 99.9 | DegreesCelsius | R
9 | Compressor 1 Suction Temperature | InputRegister | 570 | Real | AnalogValue | A919 | 1209 | -999.9 | 999.9 | DegreesCelsius | R
9 | Compressor 1 Discharge Temperature | InputRegister | 572 | Real | AnalogValue | A920 | 1210 | -999.9 | 999.9 | DegreesCelsius | R
9 | Compressor 1 Suction SuperHeat | InputRegister | 574 | Real | AnalogValue | A921 | 1211 | -99.9 | 99.9 | DegreesCelsius | R
9 | Compressor 1 Suction SuperHeat Target | InputRegister | 576 | Real | AnalogValue | A922 | 1212 | -99.9 | 99.9 | DegreesCelsius | R
9 | Outdoor Coil 1 Temperature | InputRegister | 578 | Real | AnalogValue | A923 | 1213 | -99.9 | 99.9 | DegreesCelsius | R
9 | Indoor Coil 1 Temperature | InputRegister | 580 | Real | AnalogValue | A924 | 1214 | -99.9 | 99.9 | DegreesCelsius | R
9 | Wall Control 1 Temperature | InputRegister | 582 | Real | AnalogValue | A925 | 1215 | -99.9 | 99.9 | DegreesCelsius | R
9 | Wall Control 2 Temperature | InputRegister | 584 | Real | AnalogValue | A926 | 1216 | -99.9 | 99.9 | DegreesCelsius | R
9 | Wall Control 3 Temperature | InputRegister | 586 | Real | AnalogValue | A927 | 1217 | -99.9 | 99.9 | DegreesCelsius | R
9 | Auxillary Sensor 1 Temperature | InputRegister | 588 | Real | AnalogValue | A928 | 1218 | -99.9 | 99.9 | DegreesCelsius | R
9 | Auxillary Sensor 2 Temperature | InputRegister | 590 | Real | AnalogValue | A929 | 1219 | -99.9 | 99.9 | DegreesCelsius | R
9 | Auxillary Sensor 3 Temperature | InputRegister | 592 | Real | AnalogValue | A930 | 1220 | -99.9 | 99.9 | DegreesCelsius | R
9 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 586 | Real | AnalogValue | A931 | 811 | 0 | 100 | Percent | R/W
9 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 588 | Real | AnalogValue | A932 | 812 | 0 | 100 | Percent | R/W
9 | Reduced Airflow Speed | HoldingRegister | 590 | Real | AnalogValue | A933 | 813 | 0 | 100 | Percent | R/W
9 | Economiser Outside Max Humidity | HoldingRegister | 592 | Real | AnalogValue | A934 | 814 | 0 | 100 | Percent | R/W
9 | Actual System Running Capacity | InputRegister | 594 | Real | AnalogValue | A935 | 1221 | 0 | 100 | Percent | R
9 | Compressor 1 Demand | InputRegister | 596 | Real | AnalogValue | A936 | 1222 | 0 | 100 | Percent | R
9 | Compressor 1 Speed | InputRegister | 598 | Real | AnalogValue | A937 | 1223 | 0 | 100 | Percent | R
9 | Indoor Coil 1 Fan Speed | InputRegister | 600 | Real | AnalogValue | A938 | 1224 | 0 | 100 | Percent | R
9 | Compressor 1 EEV position | InputRegister | 602 | Real | AnalogValue | A939 | 1225 | 0 | 100 | Percent | R
9 | Generic Analog 01 | HoldingRegister | 594 | Real | AnalogValue | A940 | 815 |  |  |  | R/W
9 | Generic Analog 02 | HoldingRegister | 596 | Real | AnalogValue | A941 | 816 |  |  |  | R/W
9 | Generic Analog 03 | HoldingRegister | 598 | Real | AnalogValue | A942 | 817 |  |  |  | R/W
9 | Generic Analog 04 | HoldingRegister | 600 | Real | AnalogValue | A943 | 818 |  |  |  | R/W
9 | Generic Analog 05 | HoldingRegister | 602 | Real | AnalogValue | A944 | 819 |  |  |  | R/W
9 | Turns the AC Off/On (0=Off, 1=On) | Coil | 240 | Bool | BinaryValue | D901 | 217 |  |  |  | R/W
9 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 241 | Bool | BinaryValue | D902 | 218 |  |  |  | R/W
9 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 242 | Bool | BinaryValue | D903 | 219 |  |  |  | R/W
9 | Set Turbo Mode (0=Off, 1=On) | Coil | 243 | Bool | BinaryValue | D904 | 220 |  |  |  | R/W
9 | Set Quiet Mode (0=Off, 1=On) | Coil | 244 | Bool | BinaryValue | D905 | 221 |  |  |  | R/W
9 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 245 | Bool | BinaryValue | D906 | 222 |  |  |  | R/W
9 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 248 | Bool | BinaryValue | D909 | 225 |  |  |  | R/W
9 | Enable Economiser (0=Off, 1=On) | Coil | 249 | Bool | BinaryValue | D910 | 226 |  |  |  | R/W
9 | Enable Humidity Control | Coil | 250 | Bool | BinaryValue | D911 | 227 |  |  |  | R/W
9 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 251 | Bool | BinaryValue | D912 | 228 |  |  |  | R/W
9 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 252 | Bool | BinaryValue | D913 | 229 |  |  |  | R/W
9 | Enable CO₂ Control (0=Off, 1=On) | Coil | 253 | Bool | BinaryValue | D914 | 230 |  |  |  | R/W
9 | Alarm Output (0=Off, 1=On) | DiscreteInput | 240 | Bool | BinaryValue | D915 | 460 |  |  |  | R
9 | Air Filter Notification | DiscreteInput | 241 | Bool | BinaryValue | D916 | 461 |  |  |  | R
9 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 244 | Bool | BinaryValue | D919 | 464 |  |  |  | R
9 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 245 | Bool | BinaryValue | D920 | 465 |  |  |  | R
9 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 246 | Bool | BinaryValue | D921 | 466 |  |  |  | R
9 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 247 | Bool | BinaryValue | D922 | 467 |  |  |  | R
9 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 248 | Bool | BinaryValue | D923 | 468 |  |  |  | R
9 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 249 | Bool | BinaryValue | D924 | 469 |  |  |  | R
9 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 250 | Bool | BinaryValue | D925 | 470 |  |  |  | R
9 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 251 | Bool | BinaryValue | D926 | 471 |  |  |  | R
9 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 252 | Bool | BinaryValue | D927 | 472 |  |  |  | R
9 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 253 | Bool | BinaryValue | D928 | 473 |  |  |  | R
9 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 254 | Bool | BinaryValue | D929 | 474 |  |  |  | R
9 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 255 | Bool | BinaryValue | D930 | 475 |  |  |  | R
9 | Compressor 1 Discharge Temp High | DiscreteInput | 256 | Bool | BinaryValue | D931 | 476 |  |  |  | R
9 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 257 | Bool | BinaryValue | D932 | 477 |  |  |  | R
9 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 258 | Bool | BinaryValue | D933 | 478 |  |  |  | R
9 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 259 | Bool | BinaryValue | D934 | 479 |  |  |  | R
9 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 260 | Bool | BinaryValue | D935 | 480 |  |  |  | R
9 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 261 | Bool | BinaryValue | D936 | 481 |  |  |  | R
9 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 262 | Bool | BinaryValue | D937 | 482 |  |  |  | R
9 | Set zone 1 (0=Off, 1=On) | Coil | 254 | Bool | BinaryValue | D938 | 231 |  |  |  | R/W
9 | Set zone 2 (0=Off, 1=On) | Coil | 255 | Bool | BinaryValue | D939 | 232 |  |  |  | R/W
9 | Set zone 3 (0=Off, 1=On) | Coil | 256 | Bool | BinaryValue | D940 | 233 |  |  |  | R/W
9 | Set zone 4 (0=Off, 1=On) | Coil | 257 | Bool | BinaryValue | D941 | 234 |  |  |  | R/W
9 | Set zone 5 (0=Off, 1=On) | Coil | 258 | Bool | BinaryValue | D942 | 235 |  |  |  | R/W
9 | Set zone 6 (0=Off, 1=On) | Coil | 259 | Bool | BinaryValue | D943 | 236 |  |  |  | R/W
9 | Set zone 7 (0=Off, 1=On) | Coil | 260 | Bool | BinaryValue | D944 | 237 |  |  |  | R/W
9 | Set zone 8 (0=Off, 1=On) | Coil | 261 | Bool | BinaryValue | D945 | 238 |  |  |  | R/W
9 | Generic Digital 1 | Coil | 262 | Bool | BinaryValue | D946 | 239 |  |  |  | R/W
9 | Generic Digital 2 | Coil | 263 | Bool | BinaryValue | D947 | 240 |  |  |  | R/W
9 | Generic Digital 3 | Coil | 264 | Bool | BinaryValue | D948 | 241 |  |  |  | R/W
9 | Generic Digital 4 | Coil | 265 | Bool | BinaryValue | D949 | 242 |  |  |  | R/W
9 | Generic Digital 5 | Coil | 266 | Bool | BinaryValue | D950 | 243 |  |  |  | R/W
9 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 604 | Int | IntegerValue | I901 | 820 | 1 | 4 |  | R/W
9 | Set Air Filter Notification Timer | HoldingRegister | 605 | Int | IntegerValue | I902 | 821 | 1 | 10000 | Hours | R/W
9 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 606 | Int | IntegerValue | I903 | 822 | 1 | 4 |  | R/W
9 | Target Airflow | HoldingRegister | 607 | Int | IntegerValue | I904 | 823 | 0 | 6000 | LitersPerSecond | R/W
9 | Enable Volumetric Airflow | HoldingRegister | 608 | Int | IntegerValue | I905 | 824 | 0 | 6000 | LitersPerSecond | R/W
9 | Indoor Pressure Filter level warning | HoldingRegister | 609 | Int | IntegerValue | I906 | 825 | 0 | 6000 | Pascals | R/W
9 | Economiser CO₂ Low Level | HoldingRegister | 610 | Int | IntegerValue | I907 | 826 | 0 | 1000 | PartsPerMillion | R/W
9 | Economiser CO₂ High Level | HoldingRegister | 611 | Int | IntegerValue | I908 | 827 | 0 | 1000 | PartsPerMillion | R/W
9 | BMS card Software version | InputRegister | 604 | Int | IntegerValue | I909 | 1226 | 0 | 32767 |  | R
9 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 605 | Int | IntegerValue | I910 | 1227 | 0 | 2 |  | R
9 | Air Filter Run Timer | InputRegister | 606 | Int | IntegerValue | I911 | 1228 | 0 | 10000 | Hours | R
9 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 607 | Int | IntegerValue | I912 | 1229 | 0 | 4 |  | R
9 | Indoor Airflow | InputRegister | 608 | Int | IntegerValue | I913 | 1230 | 0 | 6000 | LitersPerSecond | R
9 | Indoor Static Pressure | InputRegister | 609 | Int | IntegerValue | I914 | 1231 | 0 | 6000 | Pascals | R
9 | Measured CO₂ level | InputRegister | 610 | Int | IntegerValue | I915 | 1232 | 0 | 1000 | PartsPerMillion | R
9 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 611 | Int | IntegerValue | I916 | 1233 | 0 | 100 |  | R
9 | Error History Log, 1 error ago | InputRegister | 612 | Int | IntegerValue | I917 | 1234 | 0 | 100 |  | R
9 | Error History Log, 2 errors ago | InputRegister | 613 | Int | IntegerValue | I918 | 1235 | 0 | 100 |  | R
9 | Error History Log, 3 errors ago | InputRegister | 614 | Int | IntegerValue | I919 | 1236 | 0 | 100 |  | R
9 | Error History Log, 4 errors ago | InputRegister | 615 | Int | IntegerValue | I920 | 1237 | 0 | 100 |  | R
9 | Error History Log, 5 errors ago | InputRegister | 616 | Int | IntegerValue | I921 | 1238 | 0 | 100 |  | R
9 | Outdoor Unit 1 Model | InputRegister | 617 | Int | IntegerValue | I922 | 1239 | 0 | 32767 |  | R
9 | Outdoor Unit 1 Software version | InputRegister | 618 | Int | IntegerValue | I923 | 1240 | 0 | 32767 |  | R
9 | Compressor 1 Type | InputRegister | 619 | Int | IntegerValue | I924 | 1241 | 0 | 100 |  | R
9 | Compressor 1 Suction Pressure | InputRegister | 620 | Int | IntegerValue | I925 | 1242 | 0 | 6000 | KiloPascals | R
9 | Compressor 1 Discharge Pressure | InputRegister | 621 | Int | IntegerValue | I926 | 1243 | 0 | 6000 | KiloPascals | R
9 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 622 | Int | IntegerValue | I927 | 1244 | 0 | 3 |  | R
9 | Indoor Coil 1 Fan 1 Speed | InputRegister | 623 | Int | IntegerValue | I928 | 1245 | 0 | 9999 | RevolutionsPerMinute | R
9 | Generic Integer 1 | HoldingRegister | 612 | Int | IntegerValue | I929 | 828 |  |  |  | R/W
9 | Generic Integer 2 | HoldingRegister | 613 | Int | IntegerValue | I930 | 829 |  |  |  | R/W
9 | Generic Integer 3 | HoldingRegister | 614 | Int | IntegerValue | I931 | 830 |  |  |  | R/W
9 | Generic Integer 4 | HoldingRegister | 615 | Int | IntegerValue | I932 | 831 |  |  |  | R/W
9 | Generic Integer 5 | HoldingRegister | 616 | Int | IntegerValue | I933 | 832 |  |  |  | R/W
10 | Set Master Setpoint Temperature | HoldingRegister | 630 | Real | AnalogValue | A1001 | 833 | 16 | 30 | DegreesCelsius | R/W
10 | Economiser Temperature Difference | HoldingRegister | 634 | Real | AnalogValue | A1003 | 835 | 0 | 10 | DegreesCelsius | R/W
10 | Economiser Outside Min Temperature | HoldingRegister | 636 | Real | AnalogValue | A1004 | 836 | 0 | 22.5 | DegreesCelsius | R/W
10 | Economiser Outside Max Temperature | HoldingRegister | 638 | Real | AnalogValue | A1005 | 837 | 0 | 26 | DegreesCelsius | R/W
10 | Economiser Minimum Damper | HoldingRegister | 640 | Real | AnalogValue | A1006 | 838 | 0 | 10 | Volts | R/W
10 | Economiser Maximum Damper | HoldingRegister | 642 | Real | AnalogValue | A1007 | 839 | 0 | 10 | Volts | R/W
10 | Economiser Outside Max Moisture | HoldingRegister | 644 | Real | AnalogValue | A1008 | 840 | 0 | 100 | GramsPerKilogram | R/W
10 | Economiser Outside Max Dew Point | HoldingRegister | 646 | Real | AnalogValue | A1009 | 841 | 0 | 100 | DegreesCelsius | R/W
10 | Economiser Outside Max Enthalpy | HoldingRegister | 19 | Real | AnalogValue | A1010 | 526 | 0 | 100 | KilojoulesPerKilogram | R/W
10 | Economiser Enthalpy Delta | HoldingRegister | 648 | Real | AnalogValue | A1011 | 842 | 0 | 10 | KilojoulesPerKilogram | R/W
10 | Economiser CO₂ Minimum Damper | HoldingRegister | 650 | Real | AnalogValue | A1012 | 843 | 0 | 10 | Volts | R/W
10 | Economiser CO₂ Maximum Damper | HoldingRegister | 652 | Real | AnalogValue | A1013 | 844 | 0 | 10 | Volts | R/W
10 | Room Temperature | InputRegister | 632 | Real | AnalogValue | A1015 | 1247 | -99.9 | 99.9 | DegreesCelsius | R
10 | Indoor Room Temperature | InputRegister | 634 | Real | AnalogValue | A1016 | 1248 | -99.9 | 99.9 | DegreesCelsius | R
10 | Outside Temperature | InputRegister | 636 | Real | AnalogValue | A1017 | 1249 | -99.9 | 99.9 | DegreesCelsius | R
10 | Outside Air Temperature | InputRegister | 638 | Real | AnalogValue | A1018 | 1250 | -99.9 | 99.9 | DegreesCelsius | R
10 | Compressor 1 Suction Temperature | InputRegister | 640 | Real | AnalogValue | A1019 | 1251 | -999.9 | 999.9 | DegreesCelsius | R
10 | Compressor 1 Discharge Temperature | InputRegister | 642 | Real | AnalogValue | A1020 | 1252 | -999.9 | 999.9 | DegreesCelsius | R
10 | Compressor 1 Suction SuperHeat | InputRegister | 644 | Real | AnalogValue | A1021 | 1253 | -99.9 | 99.9 | DegreesCelsius | R
10 | Compressor 1 Suction SuperHeat Target | InputRegister | 646 | Real | AnalogValue | A1022 | 1254 | -99.9 | 99.9 | DegreesCelsius | R
10 | Outdoor Coil 1 Temperature | InputRegister | 648 | Real | AnalogValue | A1023 | 1255 |  |  | DegreesCelsius | R
10 | Indoor Coil 1 Temperature | InputRegister | 650 | Real | AnalogValue | A1024 | 1256 | -99.9 | 99.9 | DegreesCelsius | R
10 | Wall Control 1 Temperature | InputRegister | 652 | Real | AnalogValue | A1025 | 1257 | -99.9 | 99.9 | DegreesCelsius | R
10 | Wall Control 2 Temperature | InputRegister | 654 | Real | AnalogValue | A1026 | 1258 | -99.9 | 99.9 | DegreesCelsius | R
10 | Wall Control 3 Temperature | InputRegister | 656 | Real | AnalogValue | A1027 | 1259 | -99.9 | 99.9 | DegreesCelsius | R
10 | Auxillary Sensor 1 Temperature | InputRegister | 658 | Real | AnalogValue | A1028 | 1260 | -99.9 | 99.9 | DegreesCelsius | R
10 | Auxillary Sensor 2 Temperature | InputRegister | 660 | Real | AnalogValue | A1029 | 1261 | -99.9 | 99.9 | DegreesCelsius | R
10 | Auxillary Sensor 3 Temperature | InputRegister | 662 | Real | AnalogValue | A1030 | 1262 | -99.9 | 99.9 | DegreesCelsius | R
10 | Set System Capacity Demand (Advanced BMS mode only) | HoldingRegister | 654 | Real | AnalogValue | A1031 | 845 | 0 | 100 | Percent | R/W
10 | Set Supply Fan Speed Demand (Advanced BMS mode only) | HoldingRegister | 656 | Real | AnalogValue | A1032 | 846 | 0 | 100 | Percent | R/W
10 | Reduced Airflow Speed | HoldingRegister | 658 | Real | AnalogValue | A1033 | 847 | 0 | 100 | Percent | R/W
10 | Economiser Outside Max Humidity | HoldingRegister | 660 | Real | AnalogValue | A1034 | 848 | 0 | 100 | Percent | R/W
10 | Actual System Running Capacity | InputRegister | 664 | Real | AnalogValue | A1035 | 1263 | 0 | 100 | Percent | R
10 | Compressor 1 Demand | InputRegister | 666 | Real | AnalogValue | A1036 | 1264 | 0 | 100 | Percent | R
10 | Compressor 1 Speed | InputRegister | 668 | Real | AnalogValue | A1037 | 1265 | 0 | 100 | Percent | R
10 | Indoor Coil 1 Fan Speed | InputRegister | 670 | Real | AnalogValue | A1038 | 1266 | 0 | 100 | Percent | R
10 | Compressor 1 EEV position | InputRegister | 672 | Real | AnalogValue | A1039 | 1267 | 0 | 100 | Percent | R
10 | Generic Analog 01 | HoldingRegister | 662 | Real | AnalogValue | A1040 | 849 |  |  |  | R/W
10 | Generic Analog 02 | HoldingRegister | 664 | Real | AnalogValue | A1041 | 850 |  |  |  | R/W
10 | Generic Analog 03 | HoldingRegister | 666 | Real | AnalogValue | A1042 | 851 |  |  |  | R/W
10 | Generic Analog 04 | HoldingRegister | 668 | Real | AnalogValue | A1043 | 852 |  |  |  | R/W
10 | Generic Analog 05 | HoldingRegister | 670 | Real | AnalogValue | A1044 | 853 |  |  |  | R/W
10 | Turns the AC Off/On (0=Off, 1=On) | Coil | 270 | Bool | BinaryValue | D1001 | 244 |  |  |  | R/W
10 | Reset Air Filter Notification (0=Off, 1=Reset) | Coil | 271 | Bool | BinaryValue | D1002 | 245 |  |  |  | R/W
10 | Set Supply Fan Controls (0=Standard, 1=Continuous) | Coil | 272 | Bool | BinaryValue | D1003 | 246 |  |  |  | R/W
10 | Set Turbo Mode (0=Off, 1=On) | Coil | 273 | Bool | BinaryValue | D1004 | 247 |  |  |  | R/W
10 | Set Quiet Mode (0=Off, 1=On) | Coil | 274 | Bool | BinaryValue | D1005 | 248 |  |  |  | R/W
10 | Set Heat Request (0=Off, 1=On) (Advanced BMS mode only) | Coil | 275 | Bool | BinaryValue | D1006 | 249 |  |  |  | R/W
10 | Enable Outside Air Damper (0=Off, 1=On) | Coil | 278 | Bool | BinaryValue | D1009 | 252 |  |  |  | R/W
10 | Enable Economiser (0=Off, 1=On) | Coil | 279 | Bool | BinaryValue | D1010 | 253 |  |  |  | R/W
10 | Enable Humidity Control | Coil | 280 | Bool | BinaryValue | D1011 | 254 |  |  |  | R/W
10 | Humidity Sensor Configuration (0=Outdoor, 1=Outdoor&Indoor) | Coil | 281 | Bool | BinaryValue | D1012 | 255 |  |  |  | R/W
10 | Moisture Control Config (0=Moisture, 1=Enthalpy) | Coil | 282 | Bool | BinaryValue | D1013 | 256 |  |  |  | R/W
10 | Enable CO₂ Control (0=Off, 1=On) | Coil | 283 | Bool | BinaryValue | D1014 | 257 |  |  |  | R/W
10 | Alarm Output (0=Off, 1=On) | DiscreteInput | 270 | Bool | BinaryValue | D1015 | 483 |  |  |  | R
10 | Air Filter Notification | DiscreteInput | 271 | Bool | BinaryValue | D1016 | 484 |  |  |  | R
10 | Reduce Airflow Active (0=Off, 1=On) | DiscreteInput | 274 | Bool | BinaryValue | D1019 | 487 |  |  |  | R
10 | Remote On/Off (0=Low, 1=High) | DiscreteInput | 275 | Bool | BinaryValue | D1020 | 488 |  |  |  | R
10 | No Communication with Indoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 276 | Bool | BinaryValue | D1021 | 489 |  |  |  | R
10 | No Communication with Outdoor Unit (0=No Error, 1=Off Line) | DiscreteInput | 277 | Bool | BinaryValue | D1022 | 490 |  |  |  | R
10 | Room Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 278 | Bool | BinaryValue | D1023 | 491 |  |  |  | R
10 | Outside Air Temperature Sensor Status (0=OK, 1=Error) | DiscreteInput | 279 | Bool | BinaryValue | D1024 | 492 |  |  |  | R
10 | Compressor 1 running status (0=Off, 1=On) | DiscreteInput | 280 | Bool | BinaryValue | D1025 | 493 |  |  |  | R
10 | Compressor 1 Heating (0=Off, 1=On) | DiscreteInput | 281 | Bool | BinaryValue | D1026 | 494 |  |  |  | R
10 | Compressor 1 Unit Defrosting (0=Off, 1=Defrost) | DiscreteInput | 282 | Bool | BinaryValue | D1027 | 495 |  |  |  | R
10 | Compressor 1 LP switch (0=OK, 1=Tripped) | DiscreteInput | 283 | Bool | BinaryValue | D1028 | 496 |  |  |  | R
10 | Compressor 1 HP switch (0=OK, 1=Tripped) | DiscreteInput | 284 | Bool | BinaryValue | D1029 | 497 |  |  |  | R
10 | Compressor 1 HP or LP Lockout (0=Off, 1=Lockout) | DiscreteInput | 285 | Bool | BinaryValue | D1030 | 498 |  |  |  | R
10 | Compressor 1 Discharge Temp High | DiscreteInput | 286 | Bool | BinaryValue | D1031 | 499 |  |  |  | R
10 | Compressor 1 LP Status (0=OK, 1=Error) | DiscreteInput | 287 | Bool | BinaryValue | D1032 | 500 |  |  |  | R
10 | Compressor 1 HP Status (0=OK, 1=Error) | DiscreteInput | 288 | Bool | BinaryValue | D1033 | 501 |  |  |  | R
10 | Compressor 1 Suction Temperature Status (0=OK, 1=Error) | DiscreteInput | 289 | Bool | BinaryValue | D1034 | 502 |  |  |  | R
10 | Compressor 1 Duscharge Temperature Status (0=OK, 1=Error) | DiscreteInput | 290 | Bool | BinaryValue | D1035 | 503 |  |  |  | R
10 | Outdoor Coil Temperature Status (0=OK, 1=Error) | DiscreteInput | 291 | Bool | BinaryValue | D1036 | 504 |  |  |  | R
10 | Indoor Coil 1 Temperature Status (0=OK, 1=Error) | DiscreteInput | 292 | Bool | BinaryValue | D1037 | 505 |  |  |  | R
10 | Set zone 1 (0=Off, 1=On) | Coil | 284 | Bool | BinaryValue | D1038 | 258 |  |  |  | R/W
10 | Set zone 2 (0=Off, 1=On) | Coil | 285 | Bool | BinaryValue | D1039 | 259 |  |  |  | R/W
10 | Set zone 3 (0=Off, 1=On) | Coil | 286 | Bool | BinaryValue | D1040 | 260 |  |  |  | R/W
10 | Set zone 4 (0=Off, 1=On) | Coil | 287 | Bool | BinaryValue | D1041 | 261 |  |  |  | R/W
10 | Set zone 5 (0=Off, 1=On) | Coil | 288 | Bool | BinaryValue | D1042 | 262 |  |  |  | R/W
10 | Set zone 6 (0=Off, 1=On) | Coil | 289 | Bool | BinaryValue | D1043 | 263 |  |  |  | R/W
10 | Set zone 7 (0=Off, 1=On) | Coil | 290 | Bool | BinaryValue | D1044 | 264 |  |  |  | R/W
10 | Set zone 8 (0=Off, 1=On) | Coil | 291 | Bool | BinaryValue | D1045 | 265 |  |  |  | R/W
10 | Generic Digital 1 | Coil | 292 | Bool | BinaryValue | D1046 | 266 |  |  |  | R/W
10 | Generic Digital 2 | Coil | 293 | Bool | BinaryValue | D1047 | 267 |  |  |  | R/W
10 | Generic Digital 3 | Coil | 294 | Bool | BinaryValue | D1048 | 268 |  |  |  | R/W
10 | Generic Digital 4 | Coil | 295 | Bool | BinaryValue | D1049 | 269 |  |  |  | R/W
10 | Generic Digital 5 | Coil | 296 | Bool | BinaryValue | D1050 | 270 |  |  |  | R/W
10 | Set the Supply Fan Mode (1=low,2=medium,3=high,4=Auto) | HoldingRegister | 672 | Int | IntegerValue | I1001 | 854 | 1 | 4 |  | R/W
10 | Set Air Filter Notification Timer | HoldingRegister | 673 | Int | IntegerValue | I1002 | 855 | 1 | 10000 | Hours | R/W
10 | Mode of Operation (1=Heat only, 2=Cool only, 3=Auto c/o, 4=Fan only) | HoldingRegister | 674 | Int | IntegerValue | I1003 | 856 | 1 | 4 |  | R/W
10 | Target Airflow | HoldingRegister | 675 | Int | IntegerValue | I1004 | 857 | 0 | 6000 | LitersPerSecond | R/W
10 | Enable Volumetric Airflow | HoldingRegister | 676 | Int | IntegerValue | I1005 | 858 | 0 | 6000 | LitersPerSecond | R/W
10 | Indoor Pressure Filter level warning | HoldingRegister | 677 | Int | IntegerValue | I1006 | 859 | 0 | 6000 | Pascals | R/W
10 | Economiser CO₂ Low Level | HoldingRegister | 678 | Int | IntegerValue | I1007 | 860 | 0 | 1000 | PartsPerMillion | R/W
10 | Economiser CO₂ High Level | HoldingRegister | 679 | Int | IntegerValue | I1008 | 861 | 0 | 1000 | PartsPerMillion | R/W
10 | BMS card Software version | InputRegister | 674 | Int | IntegerValue | I1009 | 1268 | 0 | 32767 |  | R
10 | BMS Demand mode (0=No BMS, 1=Basic BMS, 2=Advanced BMS) | InputRegister | 675 | Int | IntegerValue | I1010 | 1269 | 0 | 2 |  | R
10 | Air Filter Run Timer | InputRegister | 676 | Int | IntegerValue | I1011 | 1270 | 0 | 10000 | Hours | R
10 | Demand Response (0=No DRM, 1=DRM1, 2=DRM2, 3=DRM3) | InputRegister | 677 | Int | IntegerValue | I1012 | 1271 | 0 | 4 |  | R
10 | Indoor Airflow | InputRegister | 678 | Int | IntegerValue | I1013 | 1272 | 0 | 6000 | LitersPerSecond | R
10 | Indoor Static Pressure | InputRegister | 679 | Int | IntegerValue | I1014 | 1273 | 0 | 6000 | Pascals | R
10 | Measured CO₂ level | InputRegister | 680 | Int | IntegerValue | I1015 | 1274 | 0 | 1000 | PartsPerMillion | R
10 | Current Error Code (Actron document 9590-0000-05) | InputRegister | 681 | Int | IntegerValue | I1016 | 1275 | 0 | 100 |  | R
10 | Error History Log, 1 error ago | InputRegister | 682 | Int | IntegerValue | I1017 | 1276 | 0 | 100 |  | R
10 | Error History Log, 2 errors ago | InputRegister | 683 | Int | IntegerValue | I1018 | 1277 | 0 | 100 |  | R
10 | Error History Log, 3 errors ago | InputRegister | 684 | Int | IntegerValue | I1019 | 1278 | 0 | 100 |  | R
10 | Error History Log, 4 errors ago | InputRegister | 685 | Int | IntegerValue | I1020 | 1279 | 0 | 100 |  | R
10 | Error History Log, 5 errors ago | InputRegister | 686 | Int | IntegerValue | I1021 | 1280 | 0 | 100 |  | R
10 | Outdoor Unit 1 Model | InputRegister | 687 | Int | IntegerValue | I1022 | 1281 | 0 | 32767 |  | R
10 | Outdoor Unit 1 Software version | InputRegister | 688 | Int | IntegerValue | I1023 | 1282 | 0 | 32767 |  | R
10 | Compressor 1 Type | InputRegister | 689 | Int | IntegerValue | I1024 | 1283 | 0 | 100 |  | R
10 | Compressor 1 Suction Pressure | InputRegister | 690 | Int | IntegerValue | I1025 | 1284 | 0 | 6000 | KiloPascals | R
10 | Compressor 1 Discharge Pressure | InputRegister | 691 | Int | IntegerValue | I1026 | 1285 | 0 | 6000 | KiloPascals | R
10 | Outdoor Coil 1 Fan Speed Setting (0=Off,1=Low,2=Medium,3=High) | InputRegister | 692 | Int | IntegerValue | I1027 | 1286 | 0 | 3 |  | R
10 | Indoor Coil 1 Fan 1 Speed | InputRegister | 693 | Int | IntegerValue | I1028 | 1287 | 0 | 9999 | RevolutionsPerMinute | R
10 | Generic Integer 1 | HoldingRegister | 680 | Int | IntegerValue | I1029 | 862 |  |  |  | R/W
10 | Generic Integer 2 | HoldingRegister | 681 | Int | IntegerValue | I1030 | 863 |  |  |  | R/W
10 | Generic Integer 3 | HoldingRegister | 682 | Int | IntegerValue | I1031 | 864 |  |  |  | R/W
10 | Generic Integer 4 | HoldingRegister | 683 | Int | IntegerValue | I1032 | 865 |  |  |  | R/W
10 | Generic Integer 5 | HoldingRegister | 684 | Int | IntegerValue | I1033 | 866 |  |  |  | R/W
11 | Device 11 Universal I/O - U2 | InputRegister | 702 | Real | AnalogValue | A1102 | 1289 |  |  |  | R
11 | Device 11 Universal I/O - U3 | InputRegister | 704 | Real | AnalogValue | A1103 | 1290 |  |  |  | R
11 | Device 11 Universal I/O - U4 | InputRegister | 706 | Real | AnalogValue | A1104 | 1291 |  |  |  | R
11 | Device 11 Universal I/O - U5 | InputRegister | 708 | Real | AnalogValue | A1105 | 1292 |  |  |  | R
11 | Device 11 Universal I/O - U6 | HoldingRegister | 700 | Real | AnalogValue | A1106 | 867 |  |  |  | R/W
11 | Device 11 Universal I/O - U7 | InputRegister | 712 | Real | AnalogValue | A1107 | 1293 |  |  |  | R
11 | Device 11 Universal I/O - U8 | InputRegister | 714 | Real | AnalogValue | A1108 | 1294 |  |  |  | R
11 | Device 11 Universal I/O - U9 | InputRegister | 716 | Real | AnalogValue | A1109 | 1295 |  |  |  | R
11 | Device 11 Universal I/O - U10 | InputRegister | 718 | Real | AnalogValue | A1110 | 1296 |  |  |  | R
11 | Device 11 relay 1 | Coil | 300 | Bool | BinaryValue | D1101 | 271 |  |  |  | R/W
11 | Device 11 relay 2 | Coil | 301 | Bool | BinaryValue | D1102 | 272 |  |  |  | R/W
11 | Device 11 relay 3 | Coil | 302 | Bool | BinaryValue | D1103 | 273 |  |  |  | R/W
11 | Device 11 relay 4 | Coil | 303 | Bool | BinaryValue | D1104 | 274 |  |  |  | R/W
11 | Device 11 relay 5 | Coil | 304 | Bool | BinaryValue | D1105 | 275 |  |  |  | R/W
11 | Device 11 relay 6 General Alarm | DiscreteInput | 300 | Bool | BinaryValue | D1106 | 506 |  |  |  | R
11 | Device 11 Universal I/O - U1 | DiscreteInput | 301 | Bool | BinaryValue | D1111 | 507 |  |  |  | R
11 | Device 11 Universal I/O - U2 | DiscreteInput | 302 | Bool | BinaryValue | D1112 | 508 |  |  |  | R
11 | Device 11 Universal I/O - U3 | DiscreteInput | 303 | Bool | BinaryValue | D1113 | 509 |  |  |  | R
11 | Device 11 Universal I/O - U4 | DiscreteInput | 304 | Bool | BinaryValue | D1114 | 510 |  |  |  | R
11 | Device 11 Universal I/O - U5 | DiscreteInput | 305 | Bool | BinaryValue | D1115 | 511 |  |  |  | R
11 | Device 11 Universal I/O - U7 | DiscreteInput | 307 | Bool | BinaryValue | D1117 | 513 |  |  |  | R
11 | Device 11 Universal I/O - U8 | DiscreteInput | 308 | Bool | BinaryValue | D1118 | 514 |  |  |  | R
11 | Device 11 Universal I/O - U9 | DiscreteInput | 309 | Bool | BinaryValue | D1119 | 515 |  |  |  | R
11 | Device 11 Universal I/O - U10 | DiscreteInput | 310 | Bool | BinaryValue | D1120 | 516 |  |  |  | R